## New Wateryard (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Wungok Village GPS : N=10.07358889, E=29.89319444 (Wungok Boma)-Werthen Payam, Abouny Village GPS: N=9.939001, E=29.825724 (Wunkur Boma)-Aliiny Payam ; Ayija Village GPS: N=9.88216667, E=29.94313889 (Akotweng Boma)-Nyiel Payam; Drilling and construction of 3 new water yards installed with solar panels and submersible pump;
Name of Bidder:
I | Description | Unit | Quantity required for project | Unit Cost [USD] | Total cost (USD)
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT |  |  |  | 0
1 | SOLAR SYSTEM
1.1 | Supply and installtion of a Dayliff or Lorentz solar system providing at least 36m3/day considering 6 hours of sunshine. The system shall comprise of a submersible pump and well probe, float switch, smart PSU with wireless data connect, PV Disconnect, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
2.1 | Supply and install of a parallel series solar pannels certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
3 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT
3.1 | Horizontal installation of 3 flow meters, at the inlet of the storage, and 1 per water kiosk. | pcs | 3 |  | 0
3.2 | Supply and installation of 6.0 metre high metalic stand tower for tank, evenly coated with a layer of anti-oxide paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. Tower to comply to manufacturing standards: Dead/Live load analysis to BS 6399. Wind load analysis to CP3 ch V 1972. Structural steel work to BS 5950 Part 1 1990. | LS | 1 |  | 0
3.3 | Supply and installation of 2 PVC high quality water tank of 5,000 liter each (Toptank recommended). | pcs | 2 |  | 0
3.4 | Supply and installation of 2-1/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 300 |  | 0
4 | WATER YARD SITE LAYOUT
4.1 | The borehole shall be fitted with a well head casted in a concrete platform of minimum 0.3m height and protected by a man hole with a cast iron trap fitted with a lockable system. | LS | 1 |  | 0
4.2 | Levelling of the site and laying a 300mm thickness well compacted murram of 60% minimum aggregate approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
5 | REPORTING
5.1 | Submit well completion report as per IOM template, including results of water quality analysis. | No | 1 |  | 0
BILL SUMMARY
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT | Unit | 3 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Water Yard Rehabilitation (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Abon 2 Village GPS: N=9.918025, E=29.98141389 (Waukok Boma)-Pariang Payam, - Drilling and rehabilitation of existing water yard installed with solar panels and submersible pump, Pariang County, Unity State
Name of Bidder:
I | Description | Unit | Quantity | Unit Cost | Total cost
BILL NO. 1 | PRELIMINARIES |  |  |  | 0
Notes:
| All the Bidders are requested to refer "Pricing Preamble and notes below" and works items of this Bills of Quantities shall be priced to fulfill the requirements there-in. Also see that no page or items are missing prior to pricing of this bill of quantities. | Note
| A list of typical general items are given below. However, the Bidder is requested to price only those items that may affect this Contract. | Note
| If no price has been stated against any item hereunder, the Contractor shall not be entitled to claim any money for such items even though he is obliged to execute the work or provide services described therein. Preliminary items priced by the Tenderer are deemed to include the cost of unpriced items. | Note
| Cost and expenses in connection with any other preliminary item which is not listed below, but is necessary for the due completion of works, is deemed to be included in the tender rates. | Note
1.1 | Site Facilities |  |  |  | 0
1.1.1 | Mobilization and demobilization from the site including all requirements of Guideline GHS12 - Site Establishment - Preparation works, protection of existing structures, materials and items, site boundaries, information board, office and welfare facilities, storage sites, generator, site reinstatement, safety, and security | 1 | Lump Sum |  | 0
1.1.2 | Fabricate a metal visibility plate 100 x 80 mm to be wall mounted. Art work of name board will be issued by IOM | 1 | each |  | 0
1.2 | Sites Operations |  |  |  | 0
1.2.1 | Allow for setting out of works in accordance with drawings; liaise with client to establish exact boundaries and other written information given by the Engineer and obtain written approval from the relevant government authorities for setting out, street and building lines before commencements of construction; Checking of any setting out or of any line or level by the Engineer shall not in any way relieve the Contractor of his responsibility for the accuracy thereof. | 1 | Lump Sum |  | 0
1.2.2 | Tools, plant, and scaffolding | 1 | Lump Sum |  | 0
1.2.3 | Allow for providing all necessary safety measures to workmen (provision for proper usage of Personal protective equipment (PPE)). | 1 | Lump Sum |  | 0
1.3 | Insurances, Bonds & Fees |  |  |  | 0
1.3.1 | Allow for Contractor's All Risk Insurance Policy, including third party liability and from the starting date until the defects liability certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the works, plant, materials, and equipment) which are not employers risk but are contractors risk Allow for insurance against claims for worker's compensation. Engineer's and Consultant's representatives, shall be included in the Insurance Policy. Allow for insurance against loss or damage to the works, adjacent structures, any existing overhead and/or underground services that may cause damages during the construction | 1 | Lump Sum |  | 0
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD |  |  |  | 0
4.1 | Supply and Installation of solar pump, solar panels and accessories | Unit | Quantity | Unit Rate | 0
4.1.1 | Supply and install Deep Well Submersible Pump, 4" 2 HP, 220V, 35 GPM, 400 ft Max, long life, to provide at least 48m3/day considering 8 hours of sunshine and a total dynamic head of 90m. The system shall comprise of control panel, submersible cable of at least 110m, float switch, UPVC Riser pipes and adaptor set, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
4.1.2 | Supply and install in a parallel series solar pannels 300 W and above, certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
4.2 | Water tank rehabilitation, Water distribution network and rehabilitation of existing water points. |  |  |  | 0
4.2.1 | Horizontal installation of 4 flow meters, at the inlet of the storage, and 1 per water stand tap station | pcs | 4 |  | 0
4.2.2 | Repair and modify the existing 6.6 metre high metalic stand tower, including providing metallic solar panels carrier welded to the existing stand tower at least 1m above water tank, ensuring strong bracings and all necessary support to resist effect of wind force. Ensure that the solar panel carrier is inclined and oriented appropariately. Conduct thorough check on the exisiting 20M3 metallic circular tank against any leakage, evenly coated with a layer of anti-oxide zinc phosphate paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. | LS | 1 |  | 0
4.2.3 | Supply and installation of 2-11/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 400 |  | 0
4.2.4 | Rehabilitation of 4 water points with 3 Talbot Talflow self closing taps each in hollow block and concrete masonry including construction of a drainage channel and a soak away pit. | pcs | 4 |  | 0
4.3 | SITE LAYOUT |  |  |  | 0
4.3.1 | The borehole shall be fitted with a pedestal stand casted raised at least 0.7m in a concrete platform of minimum 0.3m thick and protected by a man hole with a cast iron trap fitted with a lockable system. The well must have provision for deep meter hole to check static water level and depth of BH | LS | 1 |  | 0
4.3.2 | Levelling of the site and laying with well compacted murram of 60% minimum aggregate laid at interval not exceeding 100mm thick until 300mm thickness is achieved, as approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
4.3.3 | Supply and installation of a fence 8m x 8m to secure the solar system and the borehole (if feasible). The fence shall be constructed using Y shaped circular steel hollow section tubes of 50mm diameter by 3mm thickness or casted in a concrete (1:2:4) foundation (W: 0.3 X L: 0.3 X H: 0.7 m). The top part of the pole shall be welded with V-shaped of 500mm length and installed with razor wire of 0.9m diameter. The height of the pole above ground shall be determined by the height of the chain link supplied but should be of minimum 1.9m. The poles shall be installed 1.5 meters apart and reinforced using 3 lines of tension wire. An apron of 200mm wide shall be casted all round along the fence perimeter | LS | 1 |  | 0
4.3.4 | Installation of a gate frame constructed with 2 pieces of 100mm x 100mm x 3mm (4x4 inch) hollow section frame, each supported by an additional member placed at 60deg angle from the vertical pole. The gate itself shall be constructed with 60mm x 60mm x 3mm hollow sections shutter frame and covered with wire mesh. | LS | 1 |  | 0
4.3.5 | Fence and gate shall be evenly painted with a single layer of anti-oxyde paint and overlayed with an additional coating of grey/silver paint. | LS | 1 |  | 0
4.3.6 | Supply and installation of 2 modular all-in-one solar street lights, attached directly onto the solar frames and secured by razor wire. | pcs | 2 |  | 0
BILL SUMMARY
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD | Unit | 1 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## BILL A SUPPLY
PRICED BoQs FOR SOLAR POWERED MEAT COOLING FRIDGE AND STORAGE SYSTEM(S) IN BURTINLE TOWN - PUNTLAND-SOMALIA.
| BoQs of MEAT PROCESSING for RE based meat processing and storage systems in meat communities. powered meat processing and storage facilities supporting slaughtering, washing, packaging, and freezing. |  |  |  | CORDINATES: 7.6397217 47.8332667
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BoQs of Supply and Installation of ] (BoQs for powered meat processing and storage facilities supporting slaughtering, washing, packaging, and freezing.s (MSMEs )
A 1 | solar-powered meat processing and cold storage hubs deployed across six communities. It balances hygiene, energy resilience, and throughput in hot climates with unreliable grids.
1 | • Temperature: 15~ -18℃ • Refrigerant: R134a • Capacity: 108L-358L • Color: Silver • Style: Chest Deep • Power Source: Solar DC battery, Battery, Solar • Input voltage: 12V 24V • Solar panel: Class A Mono • Door: Single Folding • Temperature Type: Single-Temperature • After-sales Service Provided: Free spare parts • Warranty: 5 years • Operating Language: English • Application: Outdoor, garage, Commercial, Household, Hotel • App-Controlled: NO • Private Mold: Yes • Logo/Pattern: Silk screen printing • Brand Name: Quality motivated • Model Number: 2024 and after • Application: Commercial outdoor ( meat market small business) • Climate type: Arid and semi-arid lands (ASAL). Resilient to hot weather like the one for Somalia, shockproof and durable for handling in rough road. • Digital display with individual temperature control: LED display touch control panel makes temperature adjustment easy (if possible). • Free spare parts accompanied: Welcomed • Conformity with German/EU Standards ( CE) The refrigerator is required to mechanically and compatibly source power from the following specifications of electric supplying solar, that is also associated with energy storage battery. In other words, each refrigerator is accompanied by one (1) unit of below solar system: (Cost inclusive of anchorage & installation at the roof of the cold storage unit) •Solar Cell: Monocrystalline • Surface material: ETFE • Cloth color: Black • Open size: 2510 × 1100mm • Net weight 8.4 KG • Type of Connector: XT60 + Anderson + GX16 + DC • Additional design: Kickstands • Certifications: CE, FCC, ROHS, REACH • Conformity with German/ European Standards (CE ) • Standard Test Condtion: Irrandiance 1000W/㎡ • Module temperature: 25℃,AM=1.5 • Maximum power(Pm): 450W • Voltage at max power(Vmp): 18V • Current at max power(Imp): 22.2A • Open circuit voltage(Voc): 21.6V • Short circuit current(Isc): 24.2A • Temperature Coefficient of Pmax: (-0.41% /ºC) • Temperature Coefficient of Voc: (-0.33% /ºC) • Temperature Coefficient of Isc: (+0.06% /ºC) • Power Tolerance: -0%, +5% • Maximum System Voltage: 1500V DC • Maximum Series Fuse Rating: 25A • Operating Temperature: -20℃~65℃ • Noct*: 45℃ ± 2℃ • Warranty: 5 years product warranty on materials and workmanship • Power is not less than 95% in 5 years. | Unit | 6 |  | 0
2 | Battery Type Deep Cycle Sealed Lead Acid (Gel or AGM) Nominal Voltage 12V DC Capacity 150Ah (can vary between 100Ah–200Ah based on load and autonomy) Energy Storage 1.8 kWh (12V × 150Ah) Design Life 5–8 years (depending on usage and ambient temperature) Charge Efficiency ≥ 95% Discharge Depth Up to 80% DoD (Depth of Discharge) Operating Temperature -10°C to +50°C Cycle Life 1000+ cycles at 50% Depth of Discharge Dimensions (L×W×H) ~ 483 × 170 × 240 mm (varies slightly by manufacturer) Weight ~ 40–45 kg (for 150Ah) Terminal Type M8 or F12 (depends on model) Certifications ISO 9001, CE, RoHS. This including all the necessary fittings and installation of the solar system. Branding and labeling with project logo and identification number or implementer logo details as per engineers | Unit | 6 |  | 0
3 | Supply and train meat vendors on the use, maintenance of portable mechanical meat mincing machines of moderate volume capacity. (Training on the use of the mechanical mincing machines, hygiene, use of the refregerators and solar power). Cost inclusive of all necessary fittings, tests and dry runs. | Unit | 4 |  | 0
B.1 | Attached for Images is used for just visualising the requirement.
Total of Bill NO. A, BoQs of SOLAR POWERED MEAT COOLING FRIDGE AND STORAGE SYSTEMS IN MEAT COMMUNITIES., carried forward to summary |  |  |  |  | 0

## BILL B COLD STORAGE UNIT
MEAT COLD STORAGE UNIT HOUSING REGREGERATORS & MAIN MEAT MARKET REHABILITATION
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
ELEMENT NO. 1
SUBSTRUCTURES (ALL PROVISIONAL
EARTH WORKS
a | Site clearance works to clear site of any debris, stumps, dirt, rocks etc site. (This will include levelling,site setting out and survey work). | SM | 60 |  | 0
b | Excavation over the main site to clear top soil to reduced level upto 250mm | SM | 36 |  | 0
c | Allow for planking/shoring and strutting the sides of excavations | ITEM | 1 |  | 0
d | Excavate foundation trenches and column pits bases starting from the reduced level but not exceeding 1200mm depth | CM | 18 |  | 0
Disposal
e | cart away, Return, fill and ram selected excavated materials around foundation | CM | 18 |  | 0
Hardcore filling or other approved filling to S.E instructions
f | Approved hardcore filling Of 300mm or approved filling material, well compacted in layers of 300mm to the raised GL level | SM | 36 |  | 0
Damp Proof Membrane
g | Put a single layer of 1000-gauge polythene sheeting laid on blinded treated hardcore filling with a 150mm side lap. | SM | 40 |  | 0
| Earth Works Totals carried forward to substructure summary |  |  |  | 0
CONCRETE WORKS
Plain concrete class 15 in:
b | 50mm thick blinding under foundations and column pit bases | CM | 1 |  | 0
Reinforced Concrete class 20 as described in Structural Engineer's drawings in;
c | Strip foundation class 20 of 100mm | CM | 2 |  | 0
d | Column bases (400X400X500 mm) | CM | 1 |  | 0
e | 150mm thick slab | SM | 42 |  | 0
Reinforcements as in S.E Details: High Yield Ribbed Bars as in the Euro Code 3 (EN 1993): Strip Foundations
g | Bars of assorted sizes; cost inclusive of binding wire | KG | 120 |  | 0
Mesh fabric reinforcement to EuroCode 2 (EN 1992-1-1) and setting in concrete with 300mm side and end laps. Net allowance for laps.
h | BRC REF A 98 in surface. (Allow for substitute as per the S.E instruction to use pre-approved synthetic fibre-reinforced concrete) | SM | 40 |  | 0
Sawn Formwork as described to
i | Side of Column bases | SM | 10 |  | 0
ii | Edge of slab not exceeding 150mm high | LM | 10 |  | 0
FOUNDATION WALLING.
Natural pre-approved quarry stonewalling with a crushing strength of 2.5N/mm2 walling bedded and jointed in cement and sand (1:4) mortar as in:
b | 200mm thick loadbearing wall | SM | 24 |  | 0
| Concrete Works Total carried forward to sub-structure summary |  |  |  | 0
SUMMARY OF ELEMENTS 1
SUB-STRUCTURE (ALL PROVISIONAL)
| Earth Works |  |  |  | 0
| Concrete Works - Substructure |  |  |  | 0
| ELEMENT 1 TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0
ELEMENT NO.2
SUPER - STRUCTURE
Reinforcements
Reinforcements as in S.E Details: High Yield Ribbed Bars as in the Euro Code 3 (EN 1993)
Provide D10 Bars as lags for the steel stanchions 100mm dia.
Columns
| Supply and fix pre-painted steel stanchions 5.5m long fully fitted with lags for support; Heavy gauge 3mm thick dia 100mm and upto 5.5m long; This are column support structures | NO | 8 |  | 0
CONCRETE WORKS
Reinforced concrete class 25 (1:1.5:3) maximum gauge of aggregate course 25mm in:
a | Suspended columns concrete sorround. | CM | 2.4 |  | 0
Formwork to;
g | Sides of columns sorround | SM | 10 |  | 0
| Total Concrete works super structure to be carries to element 2 summary |  |  |  | 0
SUPER STRUCTURE WALLING
Approved machine cut stone walling bedded and jointed on mortar 1:4 cement sand and reinforced with hoop iron at every 3 courses in an alternating way
a | 200mm Thick external and internal walling | SM | 36 |  | 0
| Total walling to be carried to element 2 summary |  |  |  | 0
SUMMARY OF ELEMENTS 2
SUPER STRUCTURE
| Concrete Works |  |  |  | 0
| Walling |  |  |  | 0
| ELEMENT 2 TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0
ELEMENT NO.3
FINISHES
Use highly skilled labor for this item is advised, zero tolerance to errors
WALL FINISHES
New & Existing structure(s)
EXTERNAL WALL FINISHES
Cement and Sand (1:4) backing
a | Cement sand plaster on masonry surface externally to receive paint | SM | 36 |  | 0
b | Prepare and apply 1 coat of wall master on wall externally as directed by the project manager/designer. Colors as approved by the client | SM | 36 |  | 0
| Total External wall finishes to be carried to element number 3 summary |  |  |  | 0
INTERNAL WALL FINISHES
12mm two coats lime plaster as in;
c | Cement sand plaster on masonry surface internally to receive paint | SM | 36 |  | 0
d | Prepare and apply 2 skimming coats of gyproc filler on plastered surface on wall internal and finished smooth to received paint | SM | 36 |  | 0
e | Prepare and apply 2 coats of brilliant white* under coat and 2 final coats | SM | 36 |  | 0
FLOOR TILING (NEW STRUCTURE)
Cement and sand 1:3 screed
f | 12mm bed finished to receive colored non skid glazed tiles | SM | 36 |  | 0
First grade imported ceramic wall tilling of approved quality complete with coping and corner beads
a | Supply and fix (Ceramic Floor non skid Tiles - 300x600mm Shiny Finish ) tiles | SM | 36 |  | 0
| Total Internal Wall Finishes to be carried to element 3 summary |  |  |  | 0
Paint Works: Existing Structure Externally & Internally
Colors as approved by the engineer
e | Allow sum for preparation of surface including undercoat and necessary wall preparations to receive artistic imagery as instructed to put public awareness of hygiene and any messages as instructed. Must be high quality drawings as instructed plus branding the facilities | SM | 20 |  | 0
| Total painting work superstructure finishes to be carried to element 3 summary |  |  |  | 0
SUPER STRUCTURE WELDED STEEL SECTIONS & FINISHES
The ventilated superstructure as per the shop drawings.
| Supply 2100x900 medium gauge steel single leaf door, complete will all accessories, such as, 3 hinges, steel framing and a jua kali lock | NO | 1 |  | 0
e | Supply, 3 coat paint, weld, fix heavy gauge CHS, SHS, RHS sections and all lags to connect with the roofing of the cold storage structure. The section must be burglar proofed using heavy gauge mosquito mesh (24Square metres) as applicable: (Appx 24m - R.H.S 122x61, 110m - R.H.S 80x40. | LS | 1 |  | 0
| Total Steel Structure Finishes to be carried to element 3 Summary |  |  |  | 0
SUMMARY OF ELEMENTS 3
FINISHES
| External Wall Finishes |  |  |  | 0
| Internal Wall Finishes |  |  |  | 0
| Floor Finishes |  |  |  | 0
| Steel superstructure Finishes |  |  |  | 0
| ELEMENT 3 TOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0
ELEMENT 4 SUMMARY
ENERGY SAVING JIKOS COMPARTMENT(S)
Provide all materials, labor, and equipment for the fabrication and installation of a fixed, energy-efficient outdoor cooking stove (“jiko”), designed to minimize fuel consumption and smoke emissions. The jiko shall be constructed using durable masonry or metal components, with insulated combustion chamber, proper air inlet/outlet, and chimney for improved efficiency. The design must accommodate traditional cooking pots, ensure user safety, and be suitable for continuous outdoor use.
As per the pictorials the energy saving jikos are to be custom made to fit the large sized sufurias or deep sided, flat bottomed meat pots . Allow sum to provide the applicable space as per engineers' instruction and available site space. Well ventilated pipes/ chimney to curb smoke emissions through standard stainless steel pipes as shown (Each unit represents one pot rest/pot ring and all the components (Outer body, combustion chamber, pot rest, fuel feed opening, air inlet, chimney/flue (optional), insulation, ash pit, grate, and support base.) that anchors it)
| Installation of energy saving jikos sample as attached in the pictorials, with a capacity of holding 8 top rests of medium to large sized pots. | LS | 1 |  | 0
| SUMMARY OF ELEMENT NO.4 TO MAIN SUMMARY |  |  |  | 0
ELEMENT NO. 5
ROOFING
Provide all materials, labor, and equipment for the complete installation of a timber roof structure, including fabrication and fixing of trusses using seasoned cypress or approved hardwood. The trusses must be structurally sound and securely anchored to the wall plate. Works shall include all necessary fixings such as nails, bolts, metal straps, and connectors. Fix pre-painted corrugated roofing sheets of approved gauge and color, ensuring proper alignment, overlap, and water-tightness. All workmanship shall conform to structural safety standards and be subject to inspection prior to acceptance. Include ridgecaps, barge boards and an overlap of not less that 300mm all ways.
TRUSS FOR OUTDOOR EXTENSION & COLD STORAGE UNIT
| Supply and install purlins: 100X50MM | LM | 100 |  | 0
| Supply and install rafters: 100X50 | LM | 136 |  | 0
| Truss members & King Post: 100X100MM | LM | 100 |  | 0
0
| Supply and install gauge 30 IT4 box profile roofing or equivalent as per the engineers' approval | SM | 100 |  | 0
| ELEMENT NO 5 CARRIED TO MAIN SUMMARY |  |  |  | 0
MAIN SUMMARY
Summary of elements
| ELEMENT 1 - SUBSTRUCTURE |  |  |  | 0
| ELEMENT 2 - SUPER-STRUCTURE |  |  |  | 0
| ELEMENT 3 - FINISHES |  |  |  | 0
| ELEMENT 4 - ENERGY SAVING JIKOS |  |  |  | 0
| ELEMENT 5 - ROOFING |  |  |  | 0
| GRAND TOTAL |  |  |  | 0

## Summary
PRICED BoQs FOR SOLAR POWERED MEAT COOLING FRIDGE AND STORAGE SYSTEMS IN 6 COMMUNITIES.
Summary CORDINATES: 7.6397217 47.8332667
ITEM | DESCRIPTIONS | Unit | Quantity required | Total cost for Bill NO. | Overall Total cost (USD)
1 | Total of Bill NO A. PRICED BoQs FOR SOLAR POWERED MEAT COOLING FRIDGE AND STORAGE SYSTEMS IN 6 COMMUNITIES. | Meat cooling Fridge with Solirization | BILL A
2 | Total of Bill NO B: COLD STORAGE UNIT | COLD STORAGE UNIT | BILL B
Grand Total of Summary- USD $ |  |  |  |  | 0
Important Note: Ensure there is no mathematical errors