## New Wateryard (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Wungok Village GPS : N=10.07358889, E=29.89319444 (Wungok Boma)-Werthen Payam, Abouny Village GPS: N=9.939001, E=29.825724 (Wunkur Boma)-Aliiny Payam ; Ayija Village GPS: N=9.88216667, E=29.94313889 (Akotweng Boma)-Nyiel Payam; Drilling and construction of 3 new water yards installed with solar panels and submersible pump;
Name of Bidder:
I | Description | Unit | Quantity required for project | Unit Cost [USD] | Total cost (USD)
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT |  |  |  | 0
1 | SOLAR SYSTEM
1.1 | Supply and installtion of a Dayliff or Lorentz solar system providing at least 36m3/day considering 6 hours of sunshine. The system shall comprise of a submersible pump and well probe, float switch, smart PSU with wireless data connect, PV Disconnect, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
2.1 | Supply and install of a parallel series solar pannels certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
3 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT
3.1 | Horizontal installation of 3 flow meters, at the inlet of the storage, and 1 per water kiosk. | pcs | 3 |  | 0
3.2 | Supply and installation of 6.0 metre high metalic stand tower for tank, evenly coated with a layer of anti-oxide paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. Tower to comply to manufacturing standards: Dead/Live load analysis to BS 6399. Wind load analysis to CP3 ch V 1972. Structural steel work to BS 5950 Part 1 1990. | LS | 1 |  | 0
3.3 | Supply and installation of 2 PVC high quality water tank of 5,000 liter each (Toptank recommended). | pcs | 2 |  | 0
3.4 | Supply and installation of 2-1/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 300 |  | 0
4 | WATER YARD SITE LAYOUT
4.1 | The borehole shall be fitted with a well head casted in a concrete platform of minimum 0.3m height and protected by a man hole with a cast iron trap fitted with a lockable system. | LS | 1 |  | 0
4.2 | Levelling of the site and laying a 300mm thickness well compacted murram of 60% minimum aggregate approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
5 | REPORTING
5.1 | Submit well completion report as per IOM template, including results of water quality analysis. | No | 1 |  | 0
BILL SUMMARY
BILL NO 1 | WATER YARD CONSTRUCTION, DISTRIBUTION SYSTEM AND CONSTRUCTION OF WATER POINT | Unit | 3 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## Water Yard Rehabilitation (hidden)
BILL OF QUANTITIES
South Sudan Enhancing Community Resilience and Local Governance Project (ECRP)
Project Description: Abon 2 Village GPS: N=9.918025, E=29.98141389 (Waukok Boma)-Pariang Payam, - Drilling and rehabilitation of existing water yard installed with solar panels and submersible pump, Pariang County, Unity State
Name of Bidder:
I | Description | Unit | Quantity | Unit Cost | Total cost
BILL NO. 1 | PRELIMINARIES |  |  |  | 0
Notes:
| All the Bidders are requested to refer "Pricing Preamble and notes below" and works items of this Bills of Quantities shall be priced to fulfill the requirements there-in. Also see that no page or items are missing prior to pricing of this bill of quantities. | Note
| A list of typical general items are given below. However, the Bidder is requested to price only those items that may affect this Contract. | Note
| If no price has been stated against any item hereunder, the Contractor shall not be entitled to claim any money for such items even though he is obliged to execute the work or provide services described therein. Preliminary items priced by the Tenderer are deemed to include the cost of unpriced items. | Note
| Cost and expenses in connection with any other preliminary item which is not listed below, but is necessary for the due completion of works, is deemed to be included in the tender rates. | Note
1.1 | Site Facilities |  |  |  | 0
1.1.1 | Mobilization and demobilization from the site including all requirements of Guideline GHS12 - Site Establishment - Preparation works, protection of existing structures, materials and items, site boundaries, information board, office and welfare facilities, storage sites, generator, site reinstatement, safety, and security | 1 | Lump Sum |  | 0
1.1.2 | Fabricate a metal visibility plate 100 x 80 mm to be wall mounted. Art work of name board will be issued by IOM | 1 | each |  | 0
1.2 | Sites Operations |  |  |  | 0
1.2.1 | Allow for setting out of works in accordance with drawings; liaise with client to establish exact boundaries and other written information given by the Engineer and obtain written approval from the relevant government authorities for setting out, street and building lines before commencements of construction; Checking of any setting out or of any line or level by the Engineer shall not in any way relieve the Contractor of his responsibility for the accuracy thereof. | 1 | Lump Sum |  | 0
1.2.2 | Tools, plant, and scaffolding | 1 | Lump Sum |  | 0
1.2.3 | Allow for providing all necessary safety measures to workmen (provision for proper usage of Personal protective equipment (PPE)). | 1 | Lump Sum |  | 0
1.3 | Insurances, Bonds & Fees |  |  |  | 0
1.3.1 | Allow for Contractor's All Risk Insurance Policy, including third party liability and from the starting date until the defects liability certificate has been issued, the risks of personal injury, death, and loss of or damage to property (including, without limitation, the works, plant, materials, and equipment) which are not employers risk but are contractors risk Allow for insurance against claims for worker's compensation. Engineer's and Consultant's representatives, shall be included in the Insurance Policy. Allow for insurance against loss or damage to the works, adjacent structures, any existing overhead and/or underground services that may cause damages during the construction | 1 | Lump Sum |  | 0
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD |  |  |  | 0
4.1 | Supply and Installation of solar pump, solar panels and accessories | Unit | Quantity | Unit Rate | 0
4.1.1 | Supply and install Deep Well Submersible Pump, 4" 2 HP, 220V, 35 GPM, 400 ft Max, long life, to provide at least 48m3/day considering 8 hours of sunshine and a total dynamic head of 90m. The system shall comprise of control panel, submersible cable of at least 110m, float switch, UPVC Riser pipes and adaptor set, surge protector and lighting arrestor with a minimum of 1 piece of 8‐foot copper‐plated grounding rod. Design of the solar system needs to be inspected and validated by IOM prior to procurement and installation. | LS | 1 |  | 0
4.1.2 | Supply and install in a parallel series solar pannels 300 W and above, certified to ISO, IEC 61215 and 61730 (TÜV Rheinland) and CE oversized by 1.2 to 1.3 times the motor size. The solar panels shall be mounted facing North and a tilt angle of 7deg, mounted onto a fabricated frame above the storage tanks. | LS | 1 |  | 0
4.2 | Water tank rehabilitation, Water distribution network and rehabilitation of existing water points. |  |  |  | 0
4.2.1 | Horizontal installation of 4 flow meters, at the inlet of the storage, and 1 per water stand tap station | pcs | 4 |  | 0
4.2.2 | Repair and modify the existing 6.6 metre high metalic stand tower, including providing metallic solar panels carrier welded to the existing stand tower at least 1m above water tank, ensuring strong bracings and all necessary support to resist effect of wind force. Ensure that the solar panel carrier is inclined and oriented appropariately. Conduct thorough check on the exisiting 20M3 metallic circular tank against any leakage, evenly coated with a layer of anti-oxide zinc phosphate paint and overlayed with an additional coating of grey/silver paint and fitted with a hooped cat-ladder, top walkways of 2.1mm thickness and safety hand railings. | LS | 1 |  | 0
4.2.3 | Supply and installation of 2-11/2'' HDPE underground distribution and uPVC, PPR class 10 above ground pipeline and fittings. | m | 400 |  | 0
4.2.4 | Rehabilitation of 4 water points with 3 Talbot Talflow self closing taps each in hollow block and concrete masonry including construction of a drainage channel and a soak away pit. | pcs | 4 |  | 0
4.3 | SITE LAYOUT |  |  |  | 0
4.3.1 | The borehole shall be fitted with a pedestal stand casted raised at least 0.7m in a concrete platform of minimum 0.3m thick and protected by a man hole with a cast iron trap fitted with a lockable system. The well must have provision for deep meter hole to check static water level and depth of BH | LS | 1 |  | 0
4.3.2 | Levelling of the site and laying with well compacted murram of 60% minimum aggregate laid at interval not exceeding 100mm thick until 300mm thickness is achieved, as approved by the IOM Supervisor prior to installation. | LS | 1 |  | 0
4.3.3 | Supply and installation of a fence 8m x 8m to secure the solar system and the borehole (if feasible). The fence shall be constructed using Y shaped circular steel hollow section tubes of 50mm diameter by 3mm thickness or casted in a concrete (1:2:4) foundation (W: 0.3 X L: 0.3 X H: 0.7 m). The top part of the pole shall be welded with V-shaped of 500mm length and installed with razor wire of 0.9m diameter. The height of the pole above ground shall be determined by the height of the chain link supplied but should be of minimum 1.9m. The poles shall be installed 1.5 meters apart and reinforced using 3 lines of tension wire. An apron of 200mm wide shall be casted all round along the fence perimeter | LS | 1 |  | 0
4.3.4 | Installation of a gate frame constructed with 2 pieces of 100mm x 100mm x 3mm (4x4 inch) hollow section frame, each supported by an additional member placed at 60deg angle from the vertical pole. The gate itself shall be constructed with 60mm x 60mm x 3mm hollow sections shutter frame and covered with wire mesh. | LS | 1 |  | 0
4.3.5 | Fence and gate shall be evenly painted with a single layer of anti-oxyde paint and overlayed with an additional coating of grey/silver paint. | LS | 1 |  | 0
4.3.6 | Supply and installation of 2 modular all-in-one solar street lights, attached directly onto the solar frames and secured by razor wire. | pcs | 2 |  | 0
BILL SUMMARY
BILL NO. 4 | REHABILITATION OF EXISITING WATER YARD | Unit | 1 | 0 | 0
|  | GRAND TOTAL |  |  | 0

## BILL A-Borehole supplies
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE(S) SUPPORT INFRASTRUCTURAL WORKS
| BoQs PROPOSED BOREHOLE SUPPLIES & INSTALLATIONS - ROOX FARM |  |  |  | CORDINATES: 7.17532, 47.430925
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BOREHOLE SUPPLIES
A 1
The best efficiency point BEP must be considered for the selected borehole which has a head of 260m max.
NOTES: The design has an expected worst case drowdown of 230m and a 12m tank height, the expected system with all system energy loses should be able to fill the 40m3 tank in 2-3 hours, a pre-approved compatible variable Frequency drive will be installed (30Kw preferred), all surface cabling are to be XLPE/PVC armoured for the full load current, earthing with a dedicated earth conductor to motor shell & VFD ground. The inverter approach is as follows; dedicated solar pump inverter with directed PV input feeding VFD function or a DC-coupled VFD that accepts PV with an addition of a rectifier or hybrid controller if needed.
A 1.1 | Supply & Installation of Submersible pump, Grundfos SP 17 or higher series with 22kw/30HP /mS6000 motor, with matching cut-off electrodes, drop cables control panel, all accessories included such as but not limited to non return valves, VFD | Pcs | 1
A 1.2 | Provision and installation of 3''/6'' riser main pipe for the borehole with complete fittings | Pcs | 25
A 1.3 | Gate valves and control panel for the pump | Pcs | 1
A 1.4 | Allow sum for standard protections, sensors and controls: Sanitary sealing, Structural Integrity that is provide tamper resistant headworks that supports pressure, piping etc, and good drainage to ensure no ponding. Sum inclusive of a well cap and loackable cover as per engineer's approval. Label: as per Engineer' instructions. | LS | 1
B 1.1 | Allow a provisonal sum for piping from the borehole to the elevated tank at the borehole site inclusive of excavation works. (This includes all standard borehole protection works) | Item | 1
B 1.2 | Procurement & Installation of 30KVA Duos Genset, in-line direct injection 3-cylinder diesel engine/ type water cooled of four cycle | No | 1
C 1.1 | Allow a provisional sum of pre-approved water meter readers in the borehole outlet | No. | 1
C 1.2 | Allow provisonal sum of gantry at borehole site | No | 1
Total of Bill NO. A, BoQs of Borehole supplies, carried forward to summary |  |  |  |  | 0

## BILL B- Solar Support Structure
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURAL WORKS
| BoQs of PROPOSED MOUNTING SUPPORT STEEL STRUCTURE - ROOX FARM |  |  |  | CORDINATES: 7.17532, 47.430925
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | MOUNTING SUPPORT STEEL STRUCTURE
A 1 | SITE PREPARATION
A 1.1 | Clear site of all bushes and debris. Grab up roots and burn the arisings | m2 | 24
A 1.2 | Load, wheel and cart deposit and spread surplus excavated material where directed on site at a distance not exceeding 100 meters | Item | 1
SUBSTRUCTURES (PROVISIONAL)
B 1.1 | Excavations including maintaining and supporting sides and keeping free from water, mud and fallen material
B 1.2 | Top soil excavation average 200mm deep | m3 | 4.8
C 1.1 | Excavate for foundation not exceeding 0.3 meters deep, starting from stripped levels | M3 | 0.48
C 1.2 | Extra over for excavation in rock | m3 | 7.2
C 1.3 | Ditto: Column bases | M2 | 1.62
C 1.4 | Allow for keeping foundations free from water, mud, fallen materials, etc. | LS | 1
D1 | Disposal
D 1.1 | Return, fill and ram selected excavated material around foundations | m3 | 0.49
D 1.3 | Load, wheel and cart deposit and spread surplus excavated material where directed on site at a distance not exceeding 100 meters | m3 | 1.13
D 1.4 | Hardcore or other approved filling, as described
D1.5 | 300mm thick well compacted hardcore filling blinded with 25mm thick quarry dust layer to receive surface bed | M2 | 1.44
D 1.6 | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled smooth to receive polytheen sheeting (m.s) | M2 | 15
D 1.7 | Anti-termite treatment
D 1.8 | Gladiator or equal and approved chemical anti-termite treatment, executed complete by an approved specialist under a ten-year guarantee, to surfaces of blinding | M2 | 15
D 1.9 | Damp-proof membrane
D 1.10 | 1000 gauge polythene or other equal and approved damp-proof membrane, laid over blinded hardcore (m.s) with 300mm side and end laps (measured nett-allow for laps) | M2 | 15
E1 | STEEL FRAME
E 1.1 | Assemble all materials and construct a steel frame to support (Upto 64 )solar panels. The contrator is reminded to cost all materials labour: cutting, hoisting, placing welding, bolting priming with red oxide, painting and fixing of panels on the structure
E 1.2 | 50mm dia. GI pipes forming framework as described
E 1.3 | Columns
E 1.4 | 1500mm height | No. | 22.5
E 1.5 | Beams
E 1.6 | 4700mm length | No. | 28.2
E 1.7 | 2500mm length | No. | 25
F1 | 50mm x 3mm thick steel angle bars - Supports
F 1.1 | 2.5m length | No. | 30
F 1.2 | 800mm bracings | No. | 16
G1 | CONCRETE WORKS
G 1.1 | Plain concrete class 15 in:
G 1.2 | 100mm blinding | m3 | 1.5
G 1.3 | Ditto for column bases | m3 | 0.14
G 1.4 | Insitu concrete class 25/20 , vibrated and reinforced with 60mm thick maximum aggregate size in Slab
G 1.5 | 200mm thick surface bed laid in bays including all necessary formwork | m3 | 3.6
H1 | FINISHES
H 1.1 | Cement and sand (1:3) screeds, backings, beds etc 25mm Thick cement/sand (1:4) screed finish
H 1.2 | Floor slab | M2 | 18
H 1.3 | Painting: Prepare surfaces and apply three coats gloss oil paint as 'Crown' or equal and approved manufacturer(s) on concrete and masonry surfaces: measured overall on both sides | LS | 1
H 1.4 | Plastered surfaces internally and externally | LS | 1
0
Total of Bill NO. A, BoQs of MOUNTING SUPPORT STEEL STRUCTURE, carried forward to summary

## BILL C- Solar Installation
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURAL WORKS
| BoQs of PROPOSED SOLAR PROCUREMENT,DELIVERY & INSTALLATION - ROOX FARM |  |  |  | CORDINATES: 7.17532, 47.430925
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | SOLAR PROCUREMENT,DELIVERY & INSTALLATION
NOTES: The design has an expected worst case drowdown of 230m and a 12m tank height, the expected system with all system energy loses should be able to fill the 40m3 tank in 2-3 hours, a pre-approved compatible variable Frequency drive will be installed (30Kw preferred), all surface cabling are to be XLPE/PVC armoured for the full load current, earthing with a dedicated earth conductor to motor shell & VFD ground. The inverter approach is as follows; dedicated solar pump inverter with directed PV input feeding VFD function or a DC-coupled VFD that accepts PV with an addition of a rectifier or hybrid controller if needed.
A 1 | SITE PREPARATION
A 1.1 | Procurement and delivery of 550 watts solar panels, Mono Crystalline Solar Modules, | No | 64
A 1.2 | 8mm2 submersible pump 3-phase motor cable or equivalent for the system | Meter | 210
A 1.3 | Supply and installation of Well probe sensor c/w cable for dry running protection | Meter | 200
A 1.4 | Supply and installation of manual change over switch to switch between solar and generator power | No. | 1
A 1.2 | Supply and installation of a hybrid Controller- compatible with the hybrid sytem | No. | 1
A 1.5 | Supply and installation of PV Disconnect Switch compatible with the hybrid system | No. | 1
A 1.6 | Supply and installation of PV Protect | No. | 2
A 1.7 | Supply and installation of PV Combiner | No. | 2
A 1.8 | Supply and installation of Surge Protector | No. | 1
A 1.9 | Accessories | Lot | 1
A 1.2 | Allow Installation of upto 64 solar panels on already fabricated steel support structures | Lot | 1
0
Total of Bill NO. A, BoQs of Solar installations, carried forward to summary

## BILL D -New Elavated water tank
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURAL WORKS
BoQs of Elevated Water Tank 40m3 (12m high) - ROOX FARM (CORDINATES: 7.17532, 47.430925)
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | Elevated Water Tank 40m3 (12m high)
1 | Foundation
1.1 | Excavation: General excavation works for the column's foundations, depth up to 1500mm in all type of soil | m3 | 39.89
1.2 | Lean concrete (2000 x 2000mm, thickness 50mm): lean concrete, mix 1:4:8, ready to receive the the column's foundations | m3 | 1.2
1.3 | Foundations (1400 x 1400mm, thickness 600mm): reinforced concrete class 20 (nominal mix 1:2:4) with Y12 at column bases | m3 | 7.056
2 | Columns and Beams
2.1 | Columns (section: 300mmx 300mm): reinforced concrete mix 1:2:4, with high yield twisted rebar of Y12 and R6 for stirrups @200mm c/c | m3 | 5.83
2.2 | Beam (section 300x450mm), concrete class 20,nominal mix 1:2:4) with Y16 rebar and R8 for beam links | m3 | 9.32
3 | Storage tank (RC slabs and RC walls)
3.1 | Tank slab: (3400 x 6400mm, thickness 1500mm): reinforced concrete class 25 ( nominal mix 1:2:3) complete with water proofing, 12mm dia high yield square twisted bars for tank base slab | m3 | 3.264
3.2 | Water bar: 200mm water bar | Lm | 17
3.3 | Walls: (thickness 12mm and height of 2000mm) reinforced concrete class 25 ( nominal mix 1:2:3) complete with water proofing; 12mm high yield square twisted bars for tank walls | m3 | 3.384
3.4 | Cover slab: (4400 x 4400mm, thickness 150mm): reinforced concrete class 20 (nominal mix 1:2:4), 12mm high yield square twisted bars for tank cover slab | m3 | 1.984
4 | Inspection manhole and fittings
4.1 | Inspection manhole (600mm x 600mm): Reinforced concrete 50mm thick with BS mesh A142, bent up round iron bars handle and 50x50x3mm, using of Y12 HY Square twisted bars at man hole corners | unit | 0.02
4.2 | BS mesh A142 for manhole cover | m2 | 0.4
4.3 | 50x50x3mm L angle plates | lm | 16
4.4 | Fittings: supply and install all fittings for inlet, distribution and trucking outlets and overflow | LS | 1
4.5 | Ladder (500mm width,13m length): Supply and install a metallic ladder, including all anchorage points | unit | 1
5 | Finishes and Branding
| Allow lumpsum for organizational branding, preparation such as and not limited to plastering and painting all the external surfaces of the tank to achieve an aesthetically pleasing finish. | LS | 1
Total of Bill NO. A, BoQs of BoQs of Elevated Water Tank, carried forward to summary |  |  |  |  | 0

## BILL E - Distribution Piping
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURAL WORKS
| BoQs PROPOSED DISTRIBUTION SYSTEM - ROOX FARM |  |  |  | CORDINATES: 7.17532, 47.430925
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | BOREHOLE SUPPLIES
1 | Foundation
1.1 | Excavation of a trench (0.4m wide x 0.6m deep) for a total length of 1000m from borehole to the water kiosk | m3 | 240
1.2 | Install 2" uPVC pressure pipes including all necessary fittings from borehole to the water Kiosks, installed over a sand bed 7 cm thick and covered with sand for a minimum thickness of 10 cm. | M.L. | 1000
1.3 | Refill the pipeline trench with duly compacted soil free of relicts of excavation | M.L. | 1000
1.4 | Demarcation and layouts preparation | LS | 1
1.5 | Construction of chamber control Box (50x50x50cm) with all necessary fittings and accessories | Sum | 6
1.5 | Testing the system | Sum | 1
| Supply of 2 inch uPVC pressure pipes for supplying water from tank to the water kiosks | Pcs | 167
| Supply of all the fittings including elbows, tees, unions, gate valves, flow meters, stoppers etc | Pcs | 56
Total of Bill NO. A, BoQs of Piping, carried forward to summary |  |  |  |  | 0

## BILL F -Water Kiosks
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURAL WORKS
| BoQs of PROPOSED BOREHOLE WATER KIOSKS - ROOX FARM |  |  |  | CORDINATES: 7.17532, 47.430925
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | WATER KIOSKS
A 1 | Construction of water Kiosks
A 1.1 | Clearing of the site to remove top soil and other rubbish materials to an average depth of 200 mm. | m2 | 40
A 1.2 | Levelling and grading for foundation to a depth not exceeding 500mm starting from reduced level. | m3 | 18
A 1.3 | Back fill with selected material, well rammed in layers of 200mm thick and compacted at dry density and optimum moisture content to achieve 95% standard proctor. | m3 | 7
B 1.1 | Cart away excavated material. | m3 | 15
B 1.2 | 10cm thick C-20 mass concrete in water point base and on the surface of the hard core | m2 | 12
C 1.1 | 200mm Solid block or equivalent stone masonry water point wall grouted and filled with 1:3 mortar | m3 | 28
C 1.2 | Pointing stone masonry wall of water point with rich (1:3) mortar | m2 | 10
C 1.3 | 100mm cement screed on top of the water point and make a platform. | m2 | 10
D 1.2 | PIPE & ACCESSORIES
D 1.3 | PPR pipe 1'' | ml | 12
| Elbow 90 deg. dia. 1" | No. | 8
| Reducer dia. 1 ½"x1" | No. | 2
| Tee dia. 1” | No. | 2
| Faucet dia.1" | No. | 8
| Gate Valve dia. 1" | No. | 1
| Nipples dia 1 " | No. | 1
| Union dia 1 " | No. | 1
| Visibility bill board (1.2mx1m) with a 11/2 GI pipe legs and length of 3m the GI pipe should fix concrete at the bottom. | LS | 1
| Adapter PPR 1" | No. | 5
| Sub-total for One Kiosk |  |  |  | 0
| Water Kiosks subtotal for 2 kiosks |  |  |  | 0
Total of Bill NO. A, BoQs of BoQs of Water Kiosks, carried forward to summary |  |  |  |  | 0

## BILL G - Animal Troughs
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURAL WORKS
| BoQs of PROPOSED CONSTRUCTION OF ANIMAL TROUGH - ROOX FARM |  |  |  | CORDINATES: 7.17532, 47.430925
ITEM | DESCRIPTIONS | Unit | Quantity | Unit Cost [USD] | Total cost (USD)
BILL NO.A | CONSTRUCTION OF ANIMAL TROUGH
A 1 | Sub structure works
A 1.1 | Excavation Works:
A 1.2 | Excavate 80m long trench with average depth of 400mm into the rock from the elevated water tank to the water point | Item | 1
A 1.3 | Pipes and Accessories
A 1.4 | PVC pressure pipe with 3" diameter | M | 60
A 1.5 | Elbow 90 deg. dia. 3" | No | 2
A 1.6 | Reducer dia. 2 ½"x3" | No | 1
A 1.7 | Union diam 3" | No | 3
A 1.8 | Nipples 3" | No | 1
A 1.9 | Adaptor dia 3" | No | 2
A 1.10 | Socket dia 3" | No | 2
A 1.11 | Gate valve diam 3" | No | 1
A 1.2 | Excavate 400mm thick to the rock to a depth of 500mm below the ground level | CM | 6.6
A 1.13 | Place 50mm thick plain concrete for blind in 1:4:8 mix ratio | SM | 13.2
A 1.14 | 200mm thick VRC foundation concrete in 1:2:4 mix ratio | CM | 2.64
A 1.15 | 3Y10 for foundation reinforcement at 200mm C/C | Kg | 61.1111
A 1.16 | Y10 reinforcement at 250mm C/C | Kg | 49.2593
A 1.17 | Y8 reinforcement to the walling at 150mm C/C | Kg | 203.3778
A 1.18 | 200mm thick VRC walling concrete in 1:2:4 mix ratio | CM | 5.68
A 1.19 | An item for walling formwork including marine ply and timber bracing | Item | 1
A 2.0 | 150mm thick mass concrete aprone in 1:3:6 mix on the longer side walling of the water trough extended 3m from the wall on both sides with hardcore support on the bottom | LS | 1
A 2.1 | Backfilling to the tench | CM | 1.98
A 2.3 | 1:3 C/S mortor to 30mm thick wall plaster inside-out | SM | 37
A 1.2 | Total for construction of one animal trough |  |  |  | 0
| Total for construction of four animal trough |  |  | 4 | 0
Total of Bill NO. A, BoQs of animal trough, carried forward to summary |  |  |  |  | 0

## Summary
ACTIVE- PROJECT: REHABILITATION OF BOREHOLE SUPPORT INFRASTRUCTURES WORKS
Summary
ITEM | DESCRIPTIONS | Overall Total cost (USD)
1 | Total of Bill NO. D, BoQs of new construction of elevated Water Tank | 0
2 | Total of Bill NO. A, BoQs of Borehole supplies | 0
3 | Total of Bill NO. E, BoQs of distribution Pipiline to communities | 0
4 | Total of Bill NO. F, BoQs of BoQs of Water Kiosks | 0
5 | Total of Bill NO. G, BoQs of animal trough | 0
6 | Total of Bill NO. B, BoQs of MOUNTING SUPPORT STEEL STRUCTURE | 0
7 | Total of Bill NO. C, BoQs of Solar installations | 0
Grand Total of Summary- USD $ |  | 0
Important Note: Locations of boreholes to be rehabilitated, Solary systems, and pumping area will be in the following coordinates: LATITUDE 7.1780789, LONGITITUDE 47.4466765 / Contact the procurement entity for contact person