## Bill No.0.0 Prelim&demolition
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
PLOT SELECTION: GENERAL PRELIMINARIES, SITE MOBILIZATION & STRUCTURAL DEMOLITIONS
BILL OF QUANTITIES NO. 00: GENERAL PRELIMINARIES & DEMOLITIONS
Item No. | Description | Unit | Qty | Rate ($) | Amount ($)
0.1 | MOBILIZATION & SITE ESTABLISHMENT (FIDIC CLAUSE 4.1)
0.1.1 | Mobilize to site all heavy earthmoving equipment, concrete mixing plants, dumpers, and specialized civil engineering tools required for structural works. | Sum | 1 |  | 0
0.1.2 | Erect temporary site offices for the Resident Engineer / Project Engineer, fully furnished, air-conditioned, and equipped with communication lines, including routine maintenance for the contract duration. | Month | 6 |  | 0
0.1.3 | Erect temporary signboards, site security hoarding/fencing using corrugated sheets, and secure access gates around the site perimeter. | Item | 1 |  | 0
0.1.4 | Demobilize all plant, equipment, temporary offices, and clean up the site upon practical completion of the works. | Sum | 1 |  | 0
0.2 | HEALTH, SAFETY & ENVIRONMENTAL MANAGEMENT (FIDIC CLAUSE 4.18) |  |  |  | 0
0.2.1 | Implement Health and Safety (H&S) plan, including provision of personal protective equipment (PPE) for all personnel, medical first aid kits, and regular site safety orientations. | Month | 6 |  | 0
0.2.2 | Environmental mitigation works, including dust control watering, control of soil erosion, and management of waste runoff to protect the coastal marine ecosystem. | Item | 1 |  | 0
0.3 | SITE PREPARATION & CLEARANCE |  |  |  | 0
0.3.1 | Clear the site area of all bushes, shrubs, surface scrub, debris, and small trees, including grabbing up roots and removing materials off-site. | m2 | 3000 |  | 0
0.3.2 | Control and divert surface water runoff or localized groundwater inflows during early construction phases using temporary perimeter channels or pumping. | Item | 1 |  | 0
0.4 | STRUCTURAL DEMOLITIONS & HAZARDOUS WASTE REMOVAL |  |  |  | 0
0.4.1 | Demolish Block Type A (Dimension 35.0m x 9.0m) consisting of single-story masonry brick walling, reinforced concrete ring beams, roofing structure, and ground floor slabs. | m2 | 315 |  | 0
0.4.2 | Demolish Block Type B (Dimension 8.0m x 20.0m) consisting of single-story stone block masonry walling, timber trusses, sheet roofing, and ground slabs. | m2 | 160 |  | 0
0.4.3 | Demolish two runs of dilapidated external masonry/concrete boundary fence walls, total structural length of 100.0m up to 2.5m height, including clearing old foundation footprints. | m | 100 |  | 0
0.4.4 | Load, transport, and legally dispose of all generated masonry rubble, concrete chunks, scrap timber, and roofing sheets to an approved municipal dumpsite away from the hospital boundary. | Ton | 640 |  | 0
|  |  |  | Total | 0

## BILL NO.01 MAIN WARDS BLOCK
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
Bill of Quantities No. 01: Main Wards Block (Plot 1)
Bill No. 1: Substructure (Foundation Works)
Item No. | Description | Unit | Qty | Rate | Amount
1.1 | Earthworks
1.1.1 | Excavate oversite to remove topsoil and marine organic matter, average depth 150mm. | m3 | 77.925 |  | 0
1.1.2 | Excavate trenches for strip foundation footings, width 600mm, depth 1.2m from stripped level. | m3 | 189.18 |  | 0
1.1.3 | Provide, place, and compact approved granular hardcore material in 150mm layers under floor slabs. | m3 | 77.925 |  | 0
1.1.4 | Anti-termite chemical treatment applied to surface of hardcore and excavation faces. | m2 | 519.5 |  | 0
1.2 | Concrete Works (Substructure - SRPC) |  |  |  | 0
1.2.1 | 50mm thick mass concrete blinding (Class 15/20) under strip footings. | m3 | 5.255 |  | 0
1.2.2 | Reinforced concrete (Class 25/30) using SRPC cement in strip footings (600mm x 300mm). | m3 | 47.295 |  | 0
1.2.3 | Reinforced concrete (Class 25/30) using SRPC cement in ground beams (200mm x 400mm) and 150mm thick ground floor slab. | m3 | 119.965 |  | 0
1.3 | Reinforcement & Formwork |  |  |  | 0
1.3.1 | High-yield deformed steel bar reinforcement (Grade 460) to footings and ground beams. | kg | 6176 |  | 0
1.3.2 | Fabric reinforcement mesh (Ref. A142) in floor slab, including 200mm overlaps. | m2 | 432.36 |  | 0
1.3.3 | Sawn timber formwork to sides of foundations, ground beams, and edge trims. | m2 | 154.2 |  | 0
1.4 | Damp-Proofing & Marine Protection |  |  |  | 0
1.4.1 | 1000-gauge heavy-duty polythene damp-proof membrane (DPM) under floor slab. | m2 | 105.1 |  | 0
1.4.2 | Two coats of bitumen-based water/chloride-resistant emulsion coating to buried concrete faces. | m2 | 210.2 |  | 0
1.5 | Superstructure (Walling & Concrete) |  |  |  | 0
1.5.1 | Reinforced concrete Class 25/30 with chloride-inhibiting admixtures for ring beams (200x300mm) and columns. | m3 | 10.51 |  | 0
1.5.2 | Formwork to sides and soffits of columns and ring beams. | m2 | 157.65 |  | 0
1.5.3 | High-yield steel bar reinforcement in superstructure columns and beams. | kg | 2354 |  | 0
1.5.4 | Precast solid concrete block walling (200mm thick) in cement-sand mortar (1:3) for external perimeters. | m2 | 560 |  | 0
1.5.5 | Precast solid concrete block walling (150mm thick) in cement-sand mortar (1:3) for internal ward partitions. | m2 | 359.625 |  | 0
1.6 | Roofing & Ceiling Systems
1.6.1 | Marine-grade treated timber roof structure including trusses, purlins, and wall plates. | m2 | 675.35 |  | 0
1.6.2 | Gauge 28 Pre-painted Aluzinc (PPGL) corrugated roof sheeting with marine-grade PVDF coating, fixed to timber purlins with corrosion-resistant EPDM-washered roofing screws, all in accordance with Technical Specification. | m2 | 675.35 |  | 0
1.6.3 | Matching Gauge 28 pre-painted GI ridge caps and flashings. | m | 160 |  | 0
1.6.4 | 600x600mm False Ceiling Tiles (Moisture-resistant, anti-microbial medical grade) on anti-corrosive aluminum T-grid. | m2 | 519.5 |  | 0
1.7 | Windows & Doors)
1.7.1 | Powder-coated Aluminum frame sliding windows (60-micron marine finish) with 6mm tinted float glass and integrated fly-screens. | m2 | 45.96 |  | 0
1.7.2 | Heavy-duty double-leaf flush wooden doors with laminate finish for main ward access. (1.2m) | No. | 5 |  | 0
1.7.3 | Single-leaf semi-solid core flush wooden doors for administrative offices and staff stations. | No. | 5 |  | 0
1.7.4 | Heavy-duty uPVC water-resistant doors for W.C. units and wet rooms. | No. | 4 |  | 0
1.8 | Finishes & Coatings
1.8.1 | 12mm thick internal cement-sand plaster (1:4) to walls and columns, finished smooth. | m2 | 919.625 |  | 0
1.8.2 | 15mm thick external cement-sand render (1:3) with a weather-resistant wood float texture. | m2 | 919.625 |  | 0
1.8.3 | Glazed ceramic wall tiles (minimum 200x300mm) to a height of 2.1m in W.C.s, Dressing, and Nursing rooms. | m2 | 214.2 |  | 0
1.8.4 | Non-slip homogeneous ceramic floor tiles bedded in cement mortar and finished with anti-bacterial epoxy grout. | m2 | 519.5 |  | 0
1.8.5 | Premium weather-resistant, anti-fungal exterior emulsion paint applied in 3 coats. | m2 | 1839.25 |  | 0
1.8.6 | Anti-bacterial, washable vinyl silk interior emulsion paint applied in 3 coats. | m2 | 1508.5 |  | 0
1.9 | Mechanical, Electrical & Plumbing (MEP) Entry |  |  |  | 0
1.9.1 | Ceramic water closet (W.C.) suites complete with flushing apparatus and marine-grade sub-surface pipe lines. | No. | 4 |  | 0
1.9.2 | Deep-bowl stainless steel kitchen catering sinks and standard wash hand basins (WHB) complete with tap infrastructure. | No. | 4 |  | 0
1.9.3 | LED surface/recessed clean panel lighting luminaires integrated neatly into the ceiling grids. | No. | 38 |  | 0
| PVC-insulated copper power and lighting networks routed through concealed fire-retardant PVC conduits. | Item | 1 |  | 0
| Total |  |  |  | 0

## BILL No. 02 OPD
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
Bill No. 02: Outpatient Department (OPD) & Diagnostics Block
Item No. | Description | Unit | Qty | Rate ($) | Amount ($)
2.1 | Earthworks & Excavation
2.1.1 | Excavate oversite to remove topsoil and coastal organic sand, average depth 150mm. | m3 | 23.079 |  | 0
2.1.2 | Excavate trenches for strip foundations, 600mm wide, depth 1.2m below stripped level. | m3 | 91.44 |  | 0
2.1.3 | Provide, lay, and compact approved granular hardcore material in 150mm layers under floor slabs. | m3 | 23.079 |  | 0
2.1.4 | Apply anti-termite treatment to chemical safety standards over compacted hardcore surfaces. | m2 | 153.86 |  | 0
2.2 | Substructure Concrete & Marine Protection (SRPC) |  |  |  | 0
2.2.1 | 50mm thick mass concrete blinding (Class 15/20) under strip footings. | m3 | 3.81 |  | 0
2.2.2 | Reinforced concrete Class 25/30 using Sulfate-Resisting Portland Cement (SRPC) in strip footings (600mmx300mm). | m3 | 22.86 |  | 0
2.2.3 | Reinforced concrete Class 25/30 using SRPC in ground beams (200mmx400mm) and 150mm thick ground floor slab. | m3 | 43.399 |  | 0
2.2.4 | High-yield deformed steel bar reinforcement (Grade 460) to sub-structural elements. | kg | 3925 |  | 0
2.2.5 | Fabric reinforcement mesh (Ref. A142) in floor slab, with 200mm minimum overlaps. | m2 | 146.9 |  | 0
2.2.6 | Apply two coats of bitumen-based water/chloride-resistant emulsion coating to all buried structural surfaces. | m2 | 138.2 |  | 0
2.3 | Superstructure Walling & Shielding |  |  |  | 0
2.3.1 | Precast solid concrete block walling (200mm thick) bedded and jointed in cement-sand mortar (1:3) for standard external walls. | m2 | 199.5 |  | 0
2.3.2 | Precast high-density solid concrete block walling (200mm thick) for X-Ray Room, fully grouted with cement mortar to ensure high-mass density for radiation protection. | m2 | 56 |  | 0
2.3.3 | Precast solid concrete block walling (150mm thick) for internal clinic partitions. | m2 | 245 |  | 0
2.4 | Superstructure Reinforced Concrete |  |  |  | 0
2.4.1 | Reinforced concrete Class 25/30 featuring chloride-inhibiting admixtures for ring beams (200mmx300mm) and structural columns. | m3 | 21.4 |  | 0
2.4.2 | Sawn timber formwork to sides and soffits of superstructure concrete members. | m2 | 172.5 |  | 0
2.4.3 | High-yield steel bar reinforcement in superstructure columns and beams. | kg | 2354 |  | 0
2.5 | Roofing & Ceiling Systems |  |  |  | 0
2.5.1 | Marine-grade treated timber roof structure including engineered trusses, purlins, and wall plates fixed to beams. | m2 | 192 |  | 0
2.5.2 | Gauge 28 Pre-painted Aluzinc (PPGL) corrugated roof sheeting with marine-grade PVDF coating, fixed to timber purlins with corrosion-resistant EPDM-washered roofing screws, all in accordance with Technical Specification. | m2 | 192 |  | 0
2.5.3 | 600x600mm False Ceiling Tiles (Moisture-resistant, anti-microbial medical grade) suspended on an anti-corrosive aluminum T-grid system. | m2 | 153.6 |  | 0
2.6 | Windows, Doors & Openings |  |  |  | 0
2.6.1 | Powder-coated Aluminum frame sliding windows with marine-grade finish (minimum coating thickness 60 microns) fitted with 6mm thick tinted float glass and integrated fly-screens. | m2 | 19.8 |  | 0
2.6.2 | Heavy-duty lead-lined single-leaf flush wooden door complete with heavy-duty frame and marine-grade handles for X-Ray room entry. | No. | 1 |  | 0
2.6.3 | Single-leaf semi-solid core flush wooden doors for consultation offices, labs, and recovery units. | No. | 11 |  | 0
2.6.4 | Grade 316 Stainless Steel architectural ironmongery kits (hinges, lever locks, overhead door closers). | Item | 1 |  | 0
2.7 | Finishes & Protective Coatings |  |  |  | 0
2.7.1 | 12mm thick internal cement-sand plastering (1:4) to walls and columns, finished smooth. | m2 | 749.6 |  | 0
2.7.2 | 15mm thick external render (1:3) applied to blockwork, finished with a wood float texture. | m2 | 242 |  | 0
2.7.3 | Non-slip homogeneous ceramic floor tiles bedded in cement mortar, finished with anti-bacterial epoxy grout. | m2 | 153.86 |  | 0
2.7.4 | Apply 1 undercoat and 2 coats of premium weather-resistant, anti-fungal exterior emulsion paint to external walls. | m2 | 242 |  | 0
2.7.5 | Apply 1 undercoat and 2 coats of anti-bacterial, washable silk vinyl emulsion paint to internal walls. | m2 | 749.6 |  | 0
2.8 | MEP Provisions |  |  |  | 0
2.8.1 | Vitreous china wash hand basins (WHB) with medical-grade elbow-operated tap fittings for labs and OPD rooms. | No. | 6 |  | 0
2.8.2 | LED cleanroom-grade recessed lighting luminaires (600mmx600mm) integrated into the false ceiling grid. | No. | 32 |  | 0
2.8.3 | PVC-insulated copper wiring in concealed fire-retardant PVC conduits for lighting and power networks. | Item | 1 |  | 0
| Total |  |  | Total | 0

## Bill No. 03 MATERNITY
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
BILL No. 03 - MATERNITY BLOCK
Item No. | Description | Unit | Qty | Rate ($) | Amount ($)
3.1 | EARTHWORKS & EXCAVATION
3.1.1 | Excavate oversite to remove topsoil and organic marine layer, average depth 150mm. | m3 | 20.079 |  | 0
3.1.2 | Excavate trenches for strip foundation footings, 600mm wide, depth 1.2m below stripped level. | m3 | 77.184 |  | 0
3.1.3 | Provide, place, and compact approved granular hardcore material in 150mm thick layers under slabs. | m3 | 20.079 |  | 0
3.1.4 | Chemical anti-termite treatment applied to internal excavation surfaces and hardcore beds. | m2 | 147.246 |  | 0
3.2 | SUBSTRUCTURE CONCRETE WORKS & PROTECTION (SRPC) |  |  |  | 0
3.2.1 | 50mm thick mass concrete blinding (Class 15/20) beneath foundation lines. | m3 | 3.216 |  | 0
3.2.2 | Reinforced concrete Class 25/30 using Sulfate-Resisting Portland Cement (SRPC) in strip footings (600mm x 300mm). | m3 | 19.296 |  | 0
3.2.3 | Reinforced concrete Class 25/30 using SRPC in ground beams (200mm x 400mm) and 150mm thick structural floor slab. | m3 | 37.231 |  | 0
3.2.4 | High-yield deformed steel bar reinforcement (Grade 460) allocated to sub-structural frames. | kg | 3620 |  | 0
3.2.5 | Fabric reinforcement mesh (Ref. A142) deployed in floor slabs with 200mm laps. | m2 | 132.1 |  | 0
3.2.6 | Two coats of premium bitumen water/chloride-resistant coating to all buried substructure concrete elements. | m2 | 126.4 |  | 0
3.3 | SUPERSTRUCTURE CONCRETE & WALLING |  |  |  | 0
3.3.1 | Reinforced concrete Class 25/30 with chloride-inhibiting admixtures for superstructure ring beams (200mm x 300mm) and structural columns. | m3 | 8.85 |  | 0
3.3.2 | Sawn timber shuttering/formwork to vertical faces of superstructure column and beam grids. | m2 | 74.2 |  | 0
3.3.3 | High-yield steel reinforcement bars engineered for superstructure frame modules. | kg | 974 |  | 0
3.3.4 | Precast solid concrete block walling (200mm thick) in cement-sand mortar (1:3) for external perimeter walls. | m2 | 161 |  | 0
3.3.5 | Precast solid concrete block walling (150mm thick) in cement-sand mortar (1:3) for internal clinical partitions and delivery rooms. | m2 | 214.2 |  | 0
3.4 | ROOFING & CEILING SYSTEMS |  |  |  | 0
3.4.1 | Marine-grade treated timber roof structure including engineered trusses, purlins, and wall plates fixed to beams. | m2 | 174.018 |  | 0
3.4.2 | Gauge 28 Pre-painted Aluzinc (PPGL) corrugated roof sheeting with marine-grade PVDF coating, fixed to timber purlins with corrosion-resistant EPDM-washered roofing screws, all in accordance with Technical Specification. | m2 | 174.018 |  | 0
3.4.3 | 600x600mm False Ceiling Tiles (Moisture-resistant, anti-microbial medical grade) on an anti-corrosive aluminum T-grid system. | m2 | 133.86 |  | 0
3.5 | WINDOWS, DOORS & OPENINGS |  |  |  | 0
3.5.1 | Powder-coated Aluminum frame sliding windows (60-micron marine finish) with 6mm tinted float glass and integrated fly-screens. | m2 | 16.44 |  | 0
3.5.2 | Heavy-duty double-leaf flush wooden doors with anti-bacterial laminate panels for delivery room entrances. | No. | 3 |  | 0
3.5.3 | Single-leaf semi-solid core flush wooden doors for mid-wife offices, scan rooms, and storage spaces. | No. | 4 |  | 0
3.5.4 | Heavy-duty uPVC water-resistant flush doors for internal W.C. facilities and wet zones. | No. | 4 |  | 0
3.5.5 | Grade 316 Stainless Steel architectural ironmongery kits (heavy-duty hinges, handles, lever locks, and overhead closers). | Item | 1 |  | 0
3.6 | FINISHES & MEDICAL COATINGS |  |  |  | 0
3.6.1 | 12mm thick internal cement-sand plastering (1:4) to blockwork and concrete faces, finished smooth. | m2 | 698.4 |  | 0
3.6.2 | 15mm thick external render (1:3) applied to blockwork structures, finished with a wood float texture. | m2 | 214.2 |  | 0
3.6.3 | Glazed ceramic wall tiles (minimum 200x300mm) up to 2.1m height in all delivery rooms and W.C. suites. | m2 | 94.6 |  | 0
3.6.4 | Non-slip homogeneous ceramic floor tiles bedded in cement mortar, finished with anti-bacterial epoxy grout. | m2 | 133.86 |  | 0
3.6.5 | Premium weather-resistant, anti-fungal exterior emulsion paint applied in 3 coats. | m2 | 214.2 |  | 0
3.6.6 | Anti-bacterial, washable vinyl silk interior emulsion paint applied in 3 coats across clinical sections. | m2 | 603.8 |  | 0
3.7 | SANITARY & ELECTRICAL PROVISIONS |  |  |  | 0
3.7.1 | Ceramic water closet (W.C.) suites complete with dual-flush systems and marine-grade connection lines. | No. | 4 |  | 0
3.7.2 | Ceramic wash hand basins (WHB) equipped with medical-grade long-lever elbow-operated tap units. | No. | 5 |  | 0
3.7.3 | LED cleanroom-grade recessed lighting panels (600mm x 600mm) sealed and integrated into the grid system. | No. | 28 |  | 0
3.7.4 | PVC-insulated copper power and lighting networks routed in concealed fire-retardant PVC conduits. | Item | 1 |  | 0
|  |  |  | Total | 0

## Bill No. 04 EMERGENCY AND
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
BILL OF QUANTITIES NO. 04: EMERGENCY & OPERATION SURGERY BLOCK
Item No. | Description | Unit | Qty | Rate ($) | Amount ($)
4.1 | EARTHWORKS & EXCAVATION
4.1.1 | Excavate oversite to remove topsoil, unstable marine sand, and organic matter to an average depth of 150mm. | m3 | 16.695 |  | 0
4.1.2 | Excavate trenches for strip foundation footings, width 600mm, depth 1.2m below stripped level. | m3 | 57.528 |  | 0
4.1.3 | Provide, lay, and compact approved granular hardcore fill material in 150mm thick layers under the main floor slab. | m3 | 20.034 |  | 0
4.1.4 | Apply chemical anti-termite treatment over all compacted hardcore surfaces and excavated trench faces. | m2 | 98.6 |  | 0
4.2 | SUBSTRUCTURE CONCRETE WORKS & PROTECTION (SRPC) |  |  |  | 0
4.2.1 | 50mm thick mass concrete blinding (Class 15/20) under strip footings. | m3 | 1.97 |  | 0
4.2.2 | Reinforced concrete Class 25/30 using Sulfate-Resisting Portland Cement (SRPC) in strip footings (600mm x 300mm). | m3 | 14.382 |  | 0
4.2.3 | Reinforced concrete Class 25/30 using SRPC cement in ground beams (200mm x 400mm) and 150mm thick ground floor slab. | m3 | 29.479 |  | 0
4.2.4 | High-yield deformed steel bar reinforcement (Grade 460) allocated to sub-structural elements. | kg | 2750 |  | 0
4.2.5 | Fabric reinforcement mesh (Ref. A142) embedded in floor slabs including 200mm minimum overlaps. | m2 | 98.6 |  | 0
4.2.6 | Apply two coats of bitumen-based water/chloride-resistant emulsion coating to all buried structural faces. | m2 | 94.2 |  | 0
4.3 | SUPERSTRUCTURE WALLING |  |  |  | 0
4.3.1 | Precast solid concrete block walling (200mm thick) bedded and jointed in cement-sand mortar (1:3) for external perimeter boundaries. | m2 | 150.5 |  | 0
4.3.2 | Precast solid concrete block walling (150mm thick) for internal clinic partitions, surgery suites, and emergency modules. | m2 | 129.15 |  | 0
4.4 | SUPERSTRUCTURE REINFORCED CONCRETE STRUCTURES |  |  |  | 0
4.4.1 | Reinforced concrete Class 25/30 featuring chloride-inhibiting admixtures for ring beams (200mm x 300mm) and structural support columns. | m3 | 6.85 |  | 0
4.4.2 | Sawn timber shuttering/formwork to vertical faces of superstructure columns and beam grids. | m2 | 58.4 |  | 0
4.4.3 | High-yield steel reinforcement bars (Grade 460) for superstructure column and ring beam modules. | kg | 724 |  | 0
4.5 | ROOFING & CEILING SYSTEMS |  |  |  | 0
4.5.1 | Marine-grade treated timber roof structure including engineered trusses, purlins, and wall plates fixed to beams. | m2 | 144.69 |  | 0
4.5.2 | Gauge 28 Pre-painted Aluzinc (PPGL) corrugated roof sheeting with marine-grade PVDF coating, fixed to timber purlins with corrosion-resistant EPDM-washered roofing screws, all in accordance with Technical Specification. | m2 | 144.69 |  | 0
4.5.3 | 600x600mm False Ceiling Tiles (Moisture-resistant, anti-microbial cleanroom medical grade) suspended on an anti-corrosive aluminum T-grid system. | m2 | 111.3 |  | 0
4.6 | WINDOWS, DOORS & OPENINGS |  |  |  | 0
4.6.1 | Powder-coated Aluminum frame sliding windows (60-micron marine finish) with 6mm tinted float glass and integrated fly-screens. | m2 | 16.92 |  | 0
4.6.2 | Heavy-duty double-leaf flush wooden doors with anti-bacterial laminate panels for direct emergency and surgery theater entries. | No. | 2 |  | 0
4.6.3 | Single-leaf semi-solid core flush wooden doors for internal recovery zones, scrub rooms, and medical storage space. | No. | 5 |  | 0
4.6.4 | Heavy-duty uPVC water-resistant flush doors for internal sanitary W.C. suites. | No. | 2 |  | 0
4.6.5 | Grade 316 Stainless Steel architectural ironmongery kits (heavy-duty hinges, levers, handles, locks, and overhead door closers). | Item | 1 |  | 0
4.7 | FINISHES & PROTECTIVE COATINGS |  |  |  | 0
4.7.1 | 12mm thick internal cement-sand plastering (1:4) to masonry walls and concrete faces, finished smooth. | m2 | 408.8 |  | 0
4.7.2 | 15mm thick external render (1:3) applied to blockwork and concrete structures, finished with a wood float texture. | m2 | 150.5 |  | 0
4.7.3 | Glazed ceramic wall tiles (minimum 200x300mm) up to 2.1m height in the operation surgery room, scrub zone, and W.C. facilities. | m2 | 76.2 |  | 0
4.7.4 | Non-slip homogeneous ceramic floor tiles bedded in cement mortar, finished with anti-bacterial epoxy grout. | m2 | 111.3 |  | 0
4.7.5 | Premium weather-resistant, anti-fungal exterior emulsion paint applied in 3 coats. | m2 | 150.5 |  | 0
4.7.6 | Anti-bacterial, washable vinyl silk interior emulsion paint applied in 3 coats across clinical sections. | m2 | 408.8 |  | 0
4.8 | SANITARY, ELECTRIC & PLUMBING (MEP) |  |  |  | 0
4.8.1 | Ceramic water closet (W.C.) suites complete with dual-flush systems and marine-grade connection lines. | No. | 2 |  | 0
4.8.2 | Ceramic wash hand basins (WHB) and specialized surgical scrub sinks equipped with medical-grade long-lever elbow-operated tap units. | No. | 4 |  | 0
4.8.3 | LED cleanroom-grade recessed lighting panels (600mm x 600mm) sealed and integrated into the false ceiling grid system. | No. | 22 |  | 0
4.8.4 | PVC-insulated copper power and lighting networks routed in concealed fire-retardant PVC conduits. | Item | 1 |  | 0
|  |  |  | Total | 0

## BILL No. 05 RESTAURANT AND SECU
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
BILL OF QUANTITIES NO. 05: RESTAURANT & SECURITY ROOM
Item No. | Description | Unit | Qty | Rate ($) | Amount ($)
5.1 | EARTHWORKS & EXCAVATION
5.1.1 | Excavate oversite to remove loose coastal sand, topsoil, and organic roots to an average depth of 150mm. | m3 | 5.439 |  | 0
5.1.2 | Excavate trenches for strip foundation footings, width 600mm, depth 1.2m below stripped ground level. | m3 | 29.952 |  | 0
5.1.3 | Provide, lay, and compact approved granular hardcore material in 150mm layers under ground slabs. | m3 | 5.439 |  | 0
5.1.4 | Apply anti-termite chemical emulsion treatment to surface of compacted hardcore and excavation trench walls. | m2 | 39.1 |  | 0
5.2 | SUBSTRUCTURE CONCRETE WORKS & PROTECTION (SRPC) |  |  |  | 0
5.2.1 | 50mm thick mass concrete blinding (Class 15/20) under strip footings. | m3 | 1.248 |  | 0
5.2.2 | Reinforced concrete Class 25/30 using Sulfate-Resisting Portland Cement (SRPC) in strip footings (600mm x 300mm). | m3 | 7.488 |  | 0
5.2.3 | Reinforced concrete Class 25/30 using SRPC in ground beams (200mm x 400mm) and 150mm thick ground floor slabs. | m3 | 12.146 |  | 0
5.2.4 | High-yield deformed steel bar reinforcement (Grade 460) to footings and ground structural frames. | kg | 1420 |  | 0
5.2.5 | Fabric reinforcement mesh (Ref. A142) embedded in restaurant and security floor slabs with 200mm overlaps. | m2 | 39.1 |  | 0
5.2.6 | Apply two coats of bitumen-based chloride/water-resistant emulsion protection to all buried concrete surfaces. | m2 | 48.8 |  | 0
5.3 | SUPERSTRUCTURE WALLING |  |  |  | 0
5.3.1 | Precast solid concrete block walling (200mm thick) bedded and jointed in cement-sand mortar (1:3) for external perimeter shells. | m2 | 131.6 |  | 0
5.3.2 | Precast solid concrete block walling (150mm thick) in cement-sand mortar (1:3) for internal kitchen, counter, and partition zones. | m2 | 14 |  | 0
5.4 | SUPERSTRUCTURE REINFORCED CONCRETE |  |  |  | 0
5.4.1 | Reinforced concrete Class 25/30 incorporating chloride-inhibiting admixtures for tie/ring beams (200mm x 300mm) and framing columns. | m3 | 3.12 |  | 0
5.4.2 | Sawn timber formwork/shuttering to vertical and horizontal faces of superstructure beams and columns. | m2 | 29.6 |  | 0
5.4.3 | High-yield deformed steel reinforcing bars (Grade 460) for superstructure column and beam skeletons. | kg | 342 |  | 0
5.5 | ROOFING & CEILING SYSTEMS |  |  |  | 0
5.5.1 | Marine-grade treated timber roof structure including engineered trusses, purlins, and wall plates fixed to beams. | m2 | 47.138 |  | 0
5.5.2 | Gauge 28 Pre-painted Aluzinc (PPGL) corrugated roof sheeting with marine-grade PVDF coating, fixed to timber purlins with corrosion-resistant EPDM-washered roofing screws, all in accordance with Technical Specification. | m2 | 47.138 |  | 0
5.5.3 | 600x600mm False Ceiling Tiles (Moisture-resistant, cleanable commercial grade) on an anti-corrosive aluminum T-grid system. | m2 | 36.6 |  | 0
5.6 | WINDOWS, DOORS & OPENINGS |  |  |  | 0
5.6.1 | Powder-coated Aluminum sliding windows (60-micron marine finish) with 6mm thick tinted glass and integrated fly-screens. | m2 | 14.4 |  | 0
5.6.2 | Heavy-duty commercial glass entrance doors with marine aluminum frames for main restaurant access. | No. | 1 |  | 0
5.6.3 | Single-leaf semi-solid core flush wooden doors for the security office and kitchen storage zones. | No. | 2 |  | 0
5.6.4 | Heavy-duty uPVC water-resistant flush doors for sanitary facilities. | No. | 1 |  | 0
5.6.5 | Grade 316 Stainless Steel architectural ironmongery kits (heavy-duty hinges, handles, locks, door stops). | Item | 1 |  | 0
5.7 | FINISHES & ARCHITECTURAL COATINGS |  |  |  | 0
5.7.1 | 12mm thick internal cement-sand plastering (1:4) to masonry and concrete block surfaces, finished smooth. | m2 | 246 |  | 0
5.7.2 | 15mm thick external render (1:3) applied to blockwork structures, finished with a rugged wood float texture. | m2 | 84.2 |  | 0
5.7.3 | Glazed ceramic wall tiles (minimum 200x300mm) up to 2.1m height in the kitchen preparation area and W.C. spaces. | m2 | 34.2 |  | 0
5.7.4 | Non-slip homogeneous ceramic floor tiles bedded in cement mortar, finished with durable epoxy tile grout. | m2 | 36.26 |  | 0
5.7.5 | Premium weather-resistant, anti-fungal exterior emulsion paint applied in 3 coats. | m2 | 84.2 |  | 0
5.7.6 | Washable, durable vinyl silk interior emulsion paint applied in 3 coats across dining and office layouts. | m2 | 211.8 |  | 0
5.8 | MEP & SANITARY INFRASTRUCTURE |  |  |  | 0
5.8.1 | Ceramic water closet (W.C.) suites complete with flushing apparatus and marine-grade sub-surface pipe lines. | No. | 1 |  | 0
5.8.2 | Deep-bowl stainless steel kitchen catering sinks and standard wash hand basins (WHB) complete with tap infrastructure. | No. | 3 |  | 0
5.8.3 | LED surface/recessed clean panel lighting luminaires integrated neatly into the ceiling grids. | No. | 12 |  | 0
5.8.4 | PVC-insulated copper power and lighting networks routed through concealed fire-retardant PVC conduits. | Item | 1 |  | 0
|  |  |  | Total | 0

## Bill NO. 06 EXTERNAL WORKS
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
PLOT SELECTION: PERIMETER FENCE, OUTSIDE TOILETS BLOCK (9 UNITS) & INCINERATOR PLATFORM
BILL OF QUANTITIES NO. 06: EXTERNAL WORKS (FENCE, TOILETS & INCINERATOR)
Item No. | Description | Unit | Qty | Rate ($) | Amount ($)
6.1 | EARTHWORKS & EXCAVATION (COMBINED PLOT)
6.1.1 | Excavate oversite to remove loose marine sand, topsoil, and organic debris average depth 150mm. | m3 | 18.4 |  | 0
6.1.2 | Excavate trenches for fence column footings, strip foundations, and external toilet block structures, depth 1.2m below stripped level. | m3 | 54.6 |  | 0
6.1.3 | Provide, lay, and compact approved granular hardcore material in 150mm layers under toilet and incinerator floor slabs. | m3 | 11.2 |  | 0
6.1.4 | Anti-termite chemical emulsion treatment applied over all compacted hardcore surfaces and structural excavation faces. | m2 | 74.5 |  | 0
6.2 | SUBSTRUCTURE CONCRETE & PROTECTION (SRPC) |  |  |  | 0
6.2.1 | 50mm thick mass concrete blinding (Class 15/20) under structural footings and fence columns. | m3 | 5.358 |  | 0
6.2.2 | Reinforced concrete Class 25/30 using Sulfate-Resisting Portland Cement (SRPC) in foundation strip footings and column bases. | m3 | 32.148 |  | 0
6.2.3 | Reinforced concrete Class 25/30 using SRPC in ground beams (200x400mm) and 150mm thick ground floor slabs for toilets and incinerator pad. | m3 | 33.466 |  | 0
6.2.4 | High-yield deformed steel bar reinforcement (Grade 460) allocated to all sub-structural frames. | kg | 2120 |  | 0
6.2.5 | Fabric reinforcement mesh (Ref. A142) embedded in structural ground slabs with 200mm minimum overlaps. | m2 | 74.5 |  | 0
6.2.6 | Apply two coats of bitumen-based chloride/water-resistant emulsion protection to all buried concrete surfaces. | m2 | 86.4 |  | 0
6.3 | PERIMETER FENCE STRUCTURE (120m Long x 2.5m High) |  |  |  | 0
6.3.1 | Precast solid concrete block walling (200mm thick) bedded and jointed in cement-sand mortar (1:3) built between concrete pillars. | m2 | 264 |  | 0
6.3.2 | Reinforced concrete Class 25/30 with chloride-inhibiting admixtures for vertical fence columns and top coping beams (200x250mm). | m3 | 7.2 |  | 0
6.3.3 | Sawn timber formwork to vertical and horizontal faces of structural fence columns and coping alignments. | m2 | 118 |  | 0
6.3.4 | High-yield steel reinforcement bars engineered for columns and tie-beam configurations. | kg | 815 |  | 0
6.3.5 | Supply and install heavy-duty 3-strand razor wire mesh with hot-dip galvanized Y-shaped brackets fixed securely along the 120m wall top beam. | m | 120 |  | 0
6.4 | EXTERNAL TOILETS (9 UNITS) SUPERSTRUCTURE & WALLING |  |  |  | 0
6.4.1 | Precast solid concrete block walling (150mm thick) bedded and jointed in cement-sand mortar (1:3) for external and internal toilet cubicle walls. | m2 | 142.5 |  | 0
6.4.2 | Reinforced concrete Class 25/30 with chloride-inhibiting admixtures for ring beams and corner tie-columns. | m3 | 4.1 |  | 0
6.5 | ROOFING & CEILING SYSTEMS (TOILETS) |  |  |  | 0
6.5.1 | Marine-grade treated timber roof structure including engineered trusses, purlins, and wall plates fixed to beams. | m2 | 68.4 |  | 0
6.5.2 | Gauge 28 Pre-painted Aluzinc (PPGL) corrugated roof sheeting with marine-grade PVDF coating, fixed to timber purlins with corrosion-resistant EPDM-washered roofing screws, all in accordance with Technical Specification. | m2 | 68.4 |  | 0
6.6 | GATES & DOORS (FENCE & TOILETS) |  |  |  | 0
6.6.1 | Heavy-duty steel structural main entrance gate, 4.0m width x 2.5m height, double-leaf swing type, complete with locking drops, heavy pillars, rollers, and anti-corrosive marine primer coating. | No. | 1 |  | 0
6.6.2 | Heavy-duty steel personnel door, 1.0m width x 2.5m height, complete with locksets, integrated into perimeter wall framework. | No. | 1 |  | 0
6.6.3 | Heavy-duty uPVC water-resistant flush doors with frames for 9 outside toilet units. | No. | 9 |  | 0
6.6.4 | Marine-grade (Grade 316 Stainless Steel) ironmongery and latch sets for all external lock configurations. | Item | 1 |  | 0
6.7 | FINISHES & COATINGS |  |  |  | 0
6.7.1 | 12mm thick internal cement-sand plastering (1:4) to toilet block walls, finished smooth. | m2 | 315 |  | 0
6.7.2 | 15mm thick external render (1:3) applied to perimeter fence surfaces and toilet external shell finished with a wood float texture. | m2 | 412 |  | 0
6.7.3 | Glazed ceramic wall tiles (minimum 200x300mm) up to 1.8m height in all 9 toilet units. | m2 | 102.6 |  | 0
6.7.4 | Non-slip homogeneous ceramic floor tiles bedded in cement mortar, finished with anti-bacterial epoxy grout. | m2 | 58.2 |  | 0
6.7.5 | Premium weather-resistant, anti-fungal exterior emulsion paint applied in 3 coats across fence and exterior facades. | m2 | 412 |  | 0
6.7.6 | Washable vinyl silk interior emulsion paint applied in 3 coats inside toilet modules. | m2 | 212.4 |  | 0
6.8 | SMALL MEDICAL INCINERATOR UNIT |  |  |  | 0
6.8.1 | High-duty refractory firebrick internal lining walling for small medical-grade double-chamber combustion incinerator. | Item | 1 |  | 0
6.8.2 | Precast engineering engineering red brick external casing structure including heavy iron furnace loading door, ash removal tray, and combustion vents. | Item | 1 |  | 0
6.8.3 | Stainless steel exhaust flue stack pipe, minimum 4.5m height above ground base, with guy-wire support anchors. | No. | 1 |  | 0
6.9 | MEP & SANITARY OUTSIDE PLUMBING |  |  |  | 0
6.9.1 | Mechanical, Electrical & Plumbing (MEP) Entry |  |  |  | 0
6.9.2 | Ceramic water closet (W.C.) suites complete with flushing apparatus and marine-grade sub-surface pipe lines. | No. | 9 |  | 0
6.9.3 | Deep-bowl stainless steel kitchen catering sinks and standard wash hand basins (WHB) complete with tap infrastructure. | No. | 3 |  | 0
6.9.4 | LED surface/recessed clean panel lighting luminaires integrated neatly into the ceiling grids. | No. | 9 |  | 0
| PVC-insulated copper power and lighting networks routed through concealed fire-retardant PVC conduits. | Item | 1 |  | 0
|  |  |  | Total | 0

## SUMMARY
SUMMARY OF BILLS OF QUANTITIES
PROJECT: ADALE HOSPITAL REHABILITATION & EXPANSION
GRAND SUMMARY SHEET
Bill No. | Description | Page / Ref | Amount ($)
Bill No. 00 | General Preliminaries & Structural Demolitions | BOQ 00 | 0
Bill No. 01 | Main Wards Block (Plot 1) | BOQ 01 | 0
Bill No. 02 | Outpatient Department (OPD) & Diagnostics Block (Plot 2) | BOQ 02 | 0
Bill No. 03 | Maternity Block (Plot 3) | BOQ 03 | 0
Bill No. 04 | Emergency & Operation Surgery Block (Plot 4) | BOQ 04 | 0
Bill No. 05 | Restaurant & Security Room (Plot 5) | BOQ 05 | 0
Bill No. 06 | External Works (120m Perimeter Fence, 9 Outside Toilets & Incinerator) | BOQ 06 | 0
SUB-TOTAL (A) | TOTAL FOR MEASURED WORKS (Carried Forward) |  | 0
ADDITIONS
Add: 5.0% | Contingency Sum for Unforeseen Variations (Subject to Project Engineer Approval) | Fixed
GRAND TOTAL | TOTAL BID PRICE CARRIED TO FORM OF TENDER (VAT Inclusive) |  | 0
Amount in Words: __________________________________________USD Dollars
Tenderer's Name: ____________________________________________
Signature & Official Stamp: _____________________________________
Date: _______________________