## Lowyacado water supply
Rehabilitation and upgrading Lowyacado water supply system
SN | Description. | Unit | Quantity | Cost $ | Total Cost $
A. Solar Power System, water pump and pipeline connection.
1 | Remover the rusted GI riser pipe and replace with Supplying and installing new 2" HDPE-PVC Riser pipe , inlcudeng all required socket, elbows and thread tape, non return valves and etc. | pcs | 3 |  | 0
2 | Replace the old solar electric wire in to a new and DC solar electric wire cable 10mm | Meter | 100 |  | 0
3 | Replace the non functioning solar pannels with new pannels 310Watt. | panels | 5 |  | 0
4 | Electrical Accessories including insulation, connectors, cable lugs, metal clips, cable trucking, , cable connectors, surge protector, lightning arrestor, earthling rod including other installation accessories etc. | Lump sum | 1 |  | 0
5 | Replace the old solar frame, with new aluminium mounting frame including vertical posts and footings for 56 pcs of solar pannels. | pcs | 56 |  | 0
6 | Install new solar invertor 15kw. | pcs | 1 |  | 0
7 | Install new submersible water pump - lawara 11kw. | pcs | 1 |  | 0
8 | Installation of 3" HDPE water pipes on 2800meters from source to tank, and from tank to kiosks including pipe fittings (like tees, Sockets , gate valves, plug, unions, adaptors, elbows etc) | Meter | 2800 |  | 0
9 | Rehabilitation of existing water kiosks including insertion of water faucets(24pcs), white washing distempering the kiosks(4), and making new 4 soak-pits for each kiosk.(soak pit dimensions will be 1m dia and 1.5m deep, filled with stones and covered concrete layer.) | Job | 4 |  | 0
10 | Installation cost and transportation of materials. | JOB | 1 |  | 0
11 | print visibility( pill-boards, kiosk and other infrastructure visibility) Taakulo engineer will direct the process. | Job | 1 |  | 0
| Grand Total |  |  |  | 0

## Asha-ado water supply
Rehabilitation and upgrading Asha-Ado water supply system
SN | Description. | Unit | Quantity | Cost $ | Total Cost $
A. Solar Power System, water pump and pipeline connection.
1 | Supply and install new submersible water pump- grundfos 1.5kw. | pcs | 1 |  | 0
2 | Replace the old solar electric wire in to a new and DC solar electric wire cable 10mm | Meter | 100 |  | 0
3 | Replace the non functioning solar pannels with new pannels 310Watt. | panels | 5 |  | 0
4 | Electrical Accessories including insulation, connectors, cable lugs, metal clips, cable trucking, , cable connectors, surge protector, lightning arrestor, earthling rod including other installation accessories etc. | Lump sum | 1 |  | 0
7 | installing new 2" HDPE-PVC Riser pipe , inlcudeng all required socket, elbows and thread tape, non return valves and etc. | pcs | 3 |  | 0
8 | Supply and Installation of 1.5" HDPE water pipes on 400meters from tank to MCH including pipe fittings (like tees, Sockets , gate valves, plug, unions, adaptors, elbows etc) | Meter | 400 |  | 0
9 | Rehabilitation of existing water kiosks including insertion of water faucets(24pcs), white washing distempering the kiosks(4), and making new 4 soak-pits for each kiosk.(soak pit dimensions will be 1m dia and 1.5m deep, filled with stones and covered concrete layer.) | Job | 4 |  | 0
10 | Installation cost and transportation of materials. | JOB | 1 |  | 0
Sub-Total A: |  |  |  |  | 0
B: Rehabilitation of animal water trough
# | Description | Unit | Qty | Rate | Total
1 | Earthwork in excavation for the hardcore around two animal troughs with dimension of 6mx length1.2mx wide x0.2m x2 | m3 | 2.88 |  | 0
2 | backfill with 20cm thick hardcore using good hard stone, well compacted and graded to contain sufficient small pieces to fill all voids. dimension of 6mx1mx0.1m 2x2. | m3 | 4.8 |  | 0
3 | Supply and cast reinforced cement concrete slab of 15cm thick with cement concrete 1:2:4 (1 cement : 2 clean coarse sand : 4 stone aggregate of 25mm down), reinforced with 8mm diameter mesh @ 15cm c/c including centering and shuttering the slab shuolbe 5% slope | M3 | 2.52 |  | 0
4 | Apply two coats of cement sand plastering, 1:3 on internal and external surfaces of the partition wall and side beams. This also includes a cement sand waterproof floor screed.38 lengthx0.6 | M2 | 23 |  | 0
5 | Supply and fix 2-inch GI inlet gate valve complete with all necessary fittings, | Pcs | 1 |  | 0
6 | print visibility( pill-boards, kiosk and other infrastructure visibility) Taakulo engineer will direct the process. | Lump sum | 1 |  | 0
Sub-Total B: 1 animal trough |  |  |  |  | 0
| Grand Total |  |  |  | 0

## Toqoshi water supply
Rehabilitation and upgrading Toqoshi water supply system
SN | Description. | Unit | Quantity | Cost $ | Total Cost $
A. Elevated storage tank & pipeline connection.
1 | Rehabilitation of existing water storage elevated tank including crack repairing, leakages, replacing inlet and outlet Gi pipes and applying new painting/ distempering the outer surface of the tank. | Job | 1 |  | 0
2 | supply and install new gian link mesh fence around the elevated water tank 40meters. The coloum posts of the fence will be ms pipes 2", and 2.5 meter hight, 50cm below ground. Coloum fooring will be 40cm*40cm *40cm depth and casted with concrete. The interval of the ms pipe coloumns will be 2m each other. | Meter | 40 |  | 0
3 | Supply and Installation of 2" HDPE water pipes on 500meters from tank to the kiosks including pipe fittings (like tees, Sockets , gate valves, plug, unions, adaptors, elbows etc) | Meter | 400 |  | 0
4 | Rehabilitation of existing water kiosks including insertion of water faucets(12pcs), repairing and rebuilding massonary stand walls, and base foundation, replastering, white washing distempering the kiosks(2), and making new 2 soak-pits for each kiosk.(soak pit dimensions will be 1m dia and 1.5m deep, filled with stones and covered concrete layer.) | Job | 2 |  | 0
5 | Installation cost and transportation of materials. | JOB | 1 |  | 0
| Subtotal. |  |  |  | 0
B: Construction of 2 New Water points- kiosks.
1 | Excavation of base foundation trench (2.4x2.8x0.3m deep) | Cu.m | 2 |  | 0
2 | Supplying and laying 250 mm approved hardcore filling spread well rammed and compacted | Cu.m | 1.7 |  | 0
3 | Supplying and laying 50 mm approved lean concrete above the hardcore, spread well and smoothed. | Cu.m | 0.36 |  | 0
4 | Construct a rubble massonary wall of 1.2m*1.6m and 0.55m high, with mortar mix ratio 1:4. | Cu.m | 1.1 |  | 0
5 | Casting 10cm thick RCC top cap above the massonary cubicle foundation with mix ration 1:2:4, and Y 12@20cm c/c for both ways. (1.2*1.6*0.1m) | Cu.m | 0.2 |  | 0
6 | Casting of Vertical RCC wall above the base water point with dimension (1.6m widht*0.7m high* 0.2m thick), mixing ration 1:2:4, Y12mm@20cm c/c with 6mm stirups. | Cu.m | 0.22 |  | 0
7 | Plumping work, including fixing Gi pipe 1", 6 peeckoks, elbows, Gi tee and gate valve. | job | 1 |  | 0
8 | Excavate Soak away pit located 4meters from the structure. The drainage channel to be linked with soak away pit with a 2" PVC drainage pipe. The Soak pit to have 1m Diameter and 1.5metres deep, filled with Hardcore. | job | 1 |  | 0
| Sub-Total B- 1 kiosk |  |  |  | 0
| Total Cost of 2 kiosks |  |  | 2 | 0
C: Rehabilitation of 1 animal water trough- goats/sheep trough.
# | Description | Unit | Qty | Rate | Total
1 | Earthwork in excavation for the hardcore around two animal troughs with dimension of 6mx length1.2mx wide x0.2m x2 | m3 | 2.88 |  | 0
2 | backfill with 20cm thick hardcore using good hard stone, well compacted and graded to contain sufficient small pieces to fill all voids. dimension of 6mx1mx0.1m 2x2. | m3 | 4.8 |  | 0
3 | Supply and cast reinforced cement concrete slab of 15cm thick with cement concrete 1:2:4 (1 cement : 2 clean coarse sand : 4 stone aggregate of 25mm down), reinforced with 8mm diameter mesh @ 15cm c/c including centering and shuttering the slab shuolbe 5% slope | M3 | 2.52 |  | 0
4 | Apply two coats of cement sand plastering, 1:3 on internal and external surfaces of the partition wall and side beams. This also includes a cement sand waterproof floor screed.38 lengthx0.6 | M2 | 23 |  | 0
5 | Supply and fix 2-inch GI inlet gate valve complete with all necessary fittings, | Pcs | 1 |  | 0
6 | print visibility( pill-boards, kiosk and other infrastructure visibility) Taakulo engineer will direct the process. | job | 1 |  | 0
Sub-Total C: |  |  |  |  | 0
Grand Total Cost.( A+B) |  |  |  |  | 0

## Summary Sheet.
SUMMARY SHEET.
Item | Description | Unit | Qty | Rate (USD) | Amount (USD)
1 | Rehabilitation and upgrading of Loyacado water supply system. | No. | 1 | 0 | 0
2 | Rehabilitation and upgrading Asha-ado water supply system | No. | 1 | 0 | 0
3 | Rehabilitation and upgrading Toqoshi water supply system | No. | 1 | 0 | 0
| GRAND TOTAL. |  |  |  | 0
`
CONTRACTOR NAME:
Signature:
Address:
Tel No:
Date:
Stamp: