## BH Rehabilitation of Shallow we
Technical Annex A1: |  |  | ITB: Reference Number: ITB- SOM-DOW-24-ITB-001
DRC to complete |  |  |  |  | Bidder to complete
| Item/Milestone Required | Delivery Location | Quantity required |  | Item/Milestone offered (name make and model with full specification) | Country of Region | Quantity Offered | PICTURES
S.No | Description of works Brief Description: CONSTRUCTION OF SHALLOW WELL | Belet- Hawa | Unit | Quantity
A | Note: Shallow well construction (Dia 3) at Ramagarore village dollow District
1.1 | Excavation including maintaining and supporting sides and keeping free from water, mud and fallen materials by bailing, pumping or otherwise -Excavate for foundation strip commencing at formation level 30m deep but not exceeding 35m deep | Dollow- Ramagarore village | CM | 70.65
1.2 | Extra-over for excavation in soft rock | Dollow- Ramagarore village | CM | 3
1.3 | Cart away and deposit surplus material as directed | Dollow- Ramagarore village | CM | 18
1.4 | FILLING 400mm thick approved natural ground material,Well compacted approved selected material | Dollow- Ramagarore village | CM | 25
1.5 | WELL LINING Vibrated Reinforced Concrete class 30(1:1:2) with 20mm thick maximum aggregate size in Well ring | Dollow- Ramagarore village | CM | 0.471
1.6 | Installation Reinforced perforated concrete casing 1500mm diameter x 100mm wall thickness x 1000mm high up to 35m depth | Dollow- Ramagarore village | No. | 22
1.7 | PLATFORM:Construction of an apron, a drain and a soak-away pit as detailed on drawings | Dollow- Ramagarore village | Item | 1
1.8 | Gravel Packing:Provide cleaned and washed gravel and packing at the bottom of the well to conduct filtration admixture,15mm thick rendering | Dollow- Ramagarore village | LS | 1
1.9 | every one hour interval at least 36 continous hours) Water recharge testing(testing of the well using electrical submersible pump, the contractor to provide necessary power, etc and proper record | Dollow- Ramagarore village | Item | 1
2 | Borehole Disinfection as detail in Specification | Dollow- Ramagarore village | Item | 1
2.1 | Analysis of Water, using field test kits;2 water sample for each of the tests including Chemical, bacterial and Turbidity tests | Dollow- Ramagarore village | Item | 1
B | SUPPLY AND INSTALL SUBMERSIBLE PUMP AND MAIN RAISER PIPES
1 | Procure and install Submersible pump Lorentz-5kw, with matching cut-off electrodes, drop cables control panel, all accessories included (Stand by Pump) | Dollow- Ramagarore village | PC | 1
2 | Supply and Install 3 inch PVC Pipe for submersible pump and connect to Elevated tank | Dollow- Ramagarore village | PC | 8
3 | T-joint | Dollow- Ramagarore village | PC | 15
4 | G-Valve(2 inch) | Dollow- Ramagarore village | PC | 6
5 | Elbo- | Dollow- Ramagarore village | PC | 20
6 | Valve socket | Dollow- Ramagarore village | kg | 8
7 | Glue fax | Dollow- Ramagarore village | PC | 15
8 | Return valve(2inch) | Dollow- Ramagarore village | cum | 4
9 | Excavation of the trunch of the water pipes 30mx0.3mx0.5m | Dollow- Ramagarore village | PCs | 7.5
PROCUREMENT OF SOLAR PANELS AND INSTALLATION
| Note:solar Installation of Raamagarore Water infrastructructure Rehabilitation well depth 13m, Static Water level 5m, Depth of Pump Installed/pump level 11m with a Pumping test, transport Provision of all required tools, equipment and construction materials and clearing of site upon arrival. | Dollow- Ramagarore village
1.1 | Supply and Install Solar Panels and Accessories of Mono Crystalline Type No. 22PCs which is CERTIFIED M2 SOLAR Producted by International Organization for Standardization(ISO) and the Efficiency between 17 - 24%// Supply and Install erect solar panel Mountain structure made of Stainless steal of 8790w or aproximately 15 kw | Dollow- Ramagarore village | NO | 22
| • Type ………………………………………......................550 – 72M • Peak Power (Pmax):……………………........................550 W • Open Circuit Voltage (Voc)…………............................ 44.8 V • Short Circuit Current (Isc)……………........................... 10.6 A • Max.Power Voltage (Vmp)…………............................. 37.5 V • Max.Power Current (Imp)……………............................. 9.62 A • Maximum System Voltage…………......…................... 1500 V • Power Tolerance:……………………..……...................+/- 3% • Dimensions (MM)……………………....….....................1950 x 992 x 40 Note: All Technical Data at a Standard test Condition AM=1.5, E=1000 W/M2, Tc=25 C0 | Dollow- Ramagarore village
1.2 | Suply and Install stainless steel Solar Pump Inverter of RS10100-3L-0012-4-X+HMGR 10KW or equivalent submersible pump (DC/AC Inverters Grundfox) Controller/ pump Inverter Input U1:3AC 380-480V 50/60Hz, 11:11.3A DC 400-800V, Output 3 0-Input V 0-320Hz, 12:12A, Power P2: 5.5kw, 400V/7.5Hp:380V IP66 AC. • working temperature: -10～+50℃ • Well sensor. • Water Tank sensor. | Dollow- Ramagarore village | No | 1
1.3 | DC Wire for Special solar cable - 40 ～+1250C Max 1000V AC/1800V DC 1x6.0 mm2 | Dollow- Ramagarore village | Meter | 300
1.4 | Combiner fuse box & small accessory • DC Combiner Fuse box • DC circuit breaker • Manual transfer switch-generator & PV Array of 100A max | Dollow- Ramagarore village | No | 1
1.5 | Case Water Proof for Solar pump inverter | Dollow- Ramagarore village | PCs | 1
1.6 | Supply and install CABLE 3 core, 3x10 mm2 | Dollow- Ramagarore village | Meter | 120
1.7 | Installation, internal wiring sundries, sensors. | Dollow- Ramagarore village | LMS | 1
1.8 | Supply and Install the Solar Ground Mounting of Golvanized Steel Ranking Structure frame with Gentel sloping of 1.6m Elevation ,1.4m@<150 and Sett off the resistance of the air space of 2mm,Bolding and welding the frame work Fix to the footing | Dollow- Ramagarore village | Kw | 3
1.9 | • Excavation Footing (600x500x500) • Reinforced concrete to bellow the ground (600x500x500) bellow the ground and • Reinforced Concrete Above the ground (500x500x500)mm above the ground with base of • Supply and fix 3 Inch Galvanized steel Pipe Class B for Columns • Supply and Fix mounting of Galvanized Steel Ranking Structure • Man powering, unti rust painting with a ranking frame of Serial and Parallel as you see the attached Drawing with a technical guidance of Engineer for 11,250Wp | Dollow- Ramagarore village | Unit | 1
| 2KM PIPELINE EXTENSION RAMAGARORE VILLAGE IN DOLLOW DISTRICT | Dollow- Ramagarore village
| Note:Construction, Excavation and Backfilling of 2000m(2km) Pipeline extension and connection to the water points from the shallow well to ramagarore water tank at Targetting village at dollow District | Dollow- Ramagarore village
1 | DISTRIBUTION OF WATER PIPELINE AND INSTALLATIONS | Dollow- Ramagarore village
| Excavation of trench for piping 2000m (2km) of length, depth 500mm, 300mm width from Water tank to the Water Point (kiosks) with a Backfilling and excavation of trench | Dollow- Ramagarore village | M3 | 400
2 | Supply and install of 2000m(2km) of High Pressure 3 Inch 50mm Pvc Pipe(PVC pipe class D, 90mm OD, 10 bar, 5.8m length) For Water Supply From shallow well to the Elevated water tank includes T-Junction with a supply of all fittings(Tap + valve,cap + union+reducer+ Elbow +stop cack & Plastic Glue) i.e | Dollow- Ramagarore village | PCs | 340
3 | Supply and install of 400Mof High Pressure 2 Inch 50mm Pvc Pipe(PVC pipe class D, 90mm OD, 10 bar, 5.8m length) from water tank to water kiosks | Dollow- Ramagarore village | PCs | 400
CONSTRUCTION OF WATER KIOSKS
The Construction of Water Points with Soak Pit And Pipeline Extension
| Construction of water Kiosk | Dollow- Ramagarore village
1.1 | Site clearance: leveling and clear unnecessary materials | Dollow- Ramagarore village | M2 | 6.7
1.2 | Excavation foundation trench and level (2.4m x 2.8 x0.4 )x2 | Dollow- Ramagarore village | M3 | 5.4
1.3 | Mass concrete of 50mm thick blinding layer (1:2:4 mix) under the foundation wall 2.4m x 2.8 x0.05) | Dollow- Ramagarore village | M3 | 0.336
1.4 | 250mm hardcore filling and well compacting for slab area(2.4mx2.8m) | Dollow- Ramagarore village | M2 | 6.72
1.5 | RC concrete (1:2:4 mix ) in conc. floor slab 15 cm thick(2.4mx2.8mx0.15m) | Dollow- Ramagarore village | M3 | 1.008
1.6 | 40cm thick masonry block walling in cement & sand mortar 1;3 mix () | Dollow- Ramagarore village | M3 | 1.152
1.7 | Construct 200mm block bended with mix ratio of 1:4cement/sand (1.6mx0.6m) | Dollow- Ramagarore village | M2 | 0.96
1.8 | Cast 20cm Mass concrete 1:3:6 mix design of the area (1.6x0.2x0.2m) | Dollow- Ramagarore village | M3 | 0.064
1.9 | External & internal plastering ,12 mm thick, cement and sand mix 1:4, with wood float finish. | Dollow- Ramagarore village | M2 | 6.2
1.1 | Apply two coats of white wash and destempering | Dollow- Ramagarore village | M2 | 6.2
1.11 | 30 mm thick 1:3 cement/sand floor screed | Dollow- Ramagarore village | M3 | 6.72
1.12 | GI pipes for water Kiosk 1'' | Dollow- Ramagarore village | Pcs | 4
1.13 | Construct Complete drainage water collection with 1000mm dia for water kiosk(Soak Pit)(1000x1500x1000)mm, cover Precast concrete and fill gravel | Dollow- Ramagarore village | M3 | 1.5
2 | Fittings on the kiosk | Dollow- Ramagarore village
2.1 | GI Reducer 2" -1" | Dollow- Ramagarore village | Pcs | 1
2.2 | 900 GI Elbow 1" | Dollow- Ramagarore village | Pcs | 2
2.3 | 1" GI Double Tee | Dollow- Ramagarore village | Pcs | 2
2.4 | 1" GI Single Tee | Dollow- Ramagarore village | Pcs | 1
2.5 | Reducer socket 1"-3/4" | Dollow- Ramagarore village | Pcs | 6
2.6 | Nipple GI | Dollow- Ramagarore village | Pcs | 6
2.7 | Branch pipes, 3/4", galvanized (long pipe 300mm threaded on both sides ) | Dollow- Ramagarore village | Pcs | 6
2.8 | G.I 3/4" taps | Dollow- Ramagarore village | No | 6
2.9 | Supply and install the water point Water Fow Meter,Awakingdemi 15mm 1/2 inch Water Meter Read of Cubic Meters for Water kiosk Using with Fittings and keep protect position See the design position | Dollow- Ramagarore village | No | 1
2 | CONSTRUCTION OF CHAIN LINK FENCE | Dollow- Ramagarore village
| Provide materials and construction of chain Link Fence made from GI pipe 2.5" dia. B-class and 1.8m clear height every 2.5 meter length, The chain link is 50mmx50mm opening and 2.7mm dim. | Dollow- Ramagarore village
2.1 | Supply and Install The chain link is 50mmx50mm opening and 2.7mm dim. Which the roll is 30mx2m(LxW) The • Area of Water kiosks: Width: 3000mm Length: 3000mm | Dollow- Ramagarore village | ML | 20
2.2 | Supply and Fix 5" of Angular for as a Columns Fixing the ground | Dollow- Ramagarore village | PCs | 8
2.3 | Construction Footing and Blinding to fix G.I Pipe, then to 30cm above the footing, and welden the Security net into G.I And fix Two sides frame door of 1.5mx1.8m | Dollow- Ramagarore village | No | 12
2.4 | Construction foundation of Marble stone and concrete above the foundation a Ground beam Lean concrete to fix the Chain Link fence 40cm above the ground floor and insert the 10cm the chain link in to the footing above the ground(20cx0.2x0.40) | Dollow- Ramagarore village | M3 | 1.6
CONSTRUCTION OF 30M3 ELEVATED TANK @8M Hight
Note:The quantities are given is The Construction 30M3, 8M Hight. Quantities to be verified if these dimensions are varied
SUB STRUCTURE
1.1 | Site clearance: clear site from vegetation, debris, unwanted material and despose it to a safe place | Dollow- Ramagarore village | LMS | 1
1.2 | Footing Excavation: Excavate 9 (1.2x1.2x1.6)m Blind for footings, level and compact well ( before receiving foundation blinding)/cut and trim all projected faces | Dollow- Ramagarore village | M3 | 20.74
1.3 | Hardcore: supply and fill 300mm 9(1.2x1.2x0.3) (imported or Excavated selected material over the ground floor compact AS PER Specification before recieving blinding | Dollow- Ramagarore village | M3 | 3.89
1.4 | Foundation Blinding: Lay 50mm thick lean 4 (1.2x1.2X0.1)m concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size AS PER SPECSabove the excavated footing and foundation trenchs, cure the blinding | Dollow- Ramagarore village | M3 | 1.296
1.5 | Footing concrete : provide and cast 9 (1.1x1.1x0.75)m R.C.C footing over the blinding mix 1:2:4 /6bags of cem/1cum of concrete ___Reinforeced with double layered Y16 deformed steel in both directions/use vibrator in accordance with specifications | Dollow- Ramagarore village | M3 | 8.17
1.6 | Ground Beam Excavation: Excavate (0.5x0.4x35.4)m foundation, level and compact well ( before receiving foundation blinding)/cut and trim all projected faces | Dollow- Ramagarore village | M3 | 7.08
1.7 | Beam Blinding: Lay 50mm thick lean (0.5x0.1x35.4)m concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size as Perspecification above the excavated footing and foundation trenchs, cure the blinding | Dollow- Ramagarore village | M3 | 1.77
1.8 | Ground TIE Beams: provide and cast (0.4x0.45x35.4m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y14 linked with Y8mm stirupps @200mm c/c | Dollow- Ramagarore village | M3 | 6.37
1.9 | Backfilling with Good Hardcore and Crashed Stone: supply and fill (imported or Excavated selected material over the ground floor compact AS PER Specification | Dollow- Ramagarore village | M3 | 7.08
2 | SUPER- STRUCTURE | Dollow- Ramagarore village
2.1 | Middle Tie Beams: provide and cast 2x(0.4x0.4x41.4m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y14 linked with Y8mm stirupps @200mm c/c | Dollow- Ramagarore village | M3 | 6.62
2.2 | Bottom Slab: Cast in place (200x4000x5000)mmThick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | Dollow- Ramagarore village | M3 | 4
2.3 | Slab Beam: provide and cast (0.4x3.8x4.8m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete Reinforeced with 4Y16 linked with Y8mm stirupps @200mm c/c | Dollow- Ramagarore village | M3 | 18.24
2.4 | Columns: Cast in place 9(0.4x0.4x8.05)m R.C.C Columns Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with 6Y16mm +R8@150mm c/c | Dollow- Ramagarore village | M3 | 11.59
2.5 | Base of Roof Slabs: Cast in place (150x4000x5000)mm Thick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | Dollow- Ramagarore village | M3 | 3
2.6 | RCC WALLS: provide and cast (200x1500x18)MM RCC Wall MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with Y10 linked with Y8mm stirupps @200mm c/c | Dollow- Ramagarore village | M3 | 5.4
2.7 | Wall Plaster: apply No 2 coats of 20mm thick plastering Mix 1:4 to intenal external walls including seiving sand and even finish as per line in levels , curing as per Field Engineer | Dollow- Ramagarore village | M2 | 10.8
2.8 | White Washing : apply No2 coats of white washing to all int.and external walls | Dollow- Ramagarore village | M2 | 10.8
2.9 | Emulsion paint: apply No2 coats of emulsion paint to all int.and external walls except where stone facing is used | Dollow- Ramagarore village | M2 | 10.8
2.1 | Manhole For during Cleaning:Provide (600mmx600mm) RCC Roof Access cover Cleaning in a future | Dollow- Ramagarore village | LMS | 1
2.11 | Roof Slabs: Cast in place (150x4000x5000)MM Thick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | Dollow- Ramagarore village | M3 | 3
2.12 | G.I pipe :Provide and install inlet pipe & over flow pipe | Dollow- Ramagarore village | PCs | 3
2.13 | provide and fix steel ladder for elevated Tank | Dollow- Ramagarore village | PCs | 1
2.14 | Provide and install Cleaning Pipe | Dollow- Ramagarore village | PCs | 1
| DRC to complete |  |  |  | Bidder to complete
| Delivery time required (days after PO signature): | 90 Days | Delivery time offered (days after PO signature):
| Delivery Terms required (Add Incoterm if necessary): | DDP | Delivery Terms offered (must include incoterm):
| Delivery Destination required: | Belet-Hawa, District | Delivery Destination offered:
| Minimum bid validity period required: | 60 Days | Bid validity period offered:
| Additional comments to bidders: |  |  |  |  | Company Name:
| 1 - Please, read all the documents carefully, then price it. 2 - The contractor must ensure full compliance with all applicable local regulations, building codes, and industry standards related to the distribution site and the work being carried out. This includes obtaining any necessary permits or licenses required for the project. 3 -The contractor should adhere to the agreed-upon delivery schedule to ensure that materials are delivered to the distribution site in a timely manner. Any delays or changes in delivery should be promptly communicated and approved by the appropriate parties. 4- The contractor is responsible for ensuring that all materials supplied meet the specified quality standards. This includes conducting quality checks, inspections, and tests on the materials to verify their compliance before delivery. 5-The contractor must prioritize occupational safety during the distribution process. This involves ensuring that all work teams or subcontractors adhere to proper safety procedures, including the use of personal protective equipment (PPE) and following safety guidelines specific to the site. Additionally, strict adherence to COVID-19 prevention guidelines and protocols is essential to protect the health and well-being of all involved. 6- Supplier will take all responsibilities of delivery facilitation including access and transportation 7-all items should be with in the standard specifications and not from sanctioned countries as Annex G clarifying |  |  |  |  | Contact Person:
Address:
Phone number:
Email Address:
Date:
Do you agree on all additional comment to bidder ?
Signed by a duly authorized company representative:
Title:
Print Name:
Stamp of company