## BOQs-BLX
FINANCIAL ANNEX A.2 - BILL OF QUANTITY |  |  |  | ITB Reference Number: ITB-SOM-CO-2025-009 (Rehabilitation of Water Infrastructure in Belethawa, Jubbaland State, Somalia).
A | BILL OF QUANTITIES FOR CONSTRUCTION OF ELEVATED 30M3 WATER TANK
S.No | DESCRIPTIONS OF WORK/ACTIVITIES | Location | UNIT | QUANTITY | Unit Price (USD) | Total Price (USD)
CONSTRUCTION OF 30M3 ELEVATED TANK @8M Hight
Note:The quantities are given is The Construction 30M3, 8M Hight. Quantities to be verified if these dimensions are varied
1 | SUB STRUCTURE
1.1 | Site clearance: clear site from vegetation, debris, unwanted material and despose it to a safe place | Belethawa | LMS | 1
1.2 | Footing Excavation: Excavate 9 (1.2x1.2x1.6)m Blind for footings, level and compact well ( before receiving foundation blinding)/cut and trim all projected faces | Belethawa | M3 | 20.74
1.3 | Hardcore: supply and fill 300mm 9(1.2x1.2x0.3) (imported or Excavated selected material over the ground floor compact AS PER Specification before recieving blinding | Belethawa | M3 | 3.89
1.4 | Foundation Blinding: Lay 50mm thick lean 4 (1.2x1.2X0.1)m concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size AS PER SPECSabove the excavated footing and foundation trenchs, cure the blinding | Belethawa | M3 | 1.296
1.5 | Footing concrete : provide and cast 9 (1.1x1.1x0.75)m R.C.C footing over the blinding mix 1:2:4 /6bags of cem/1cum of concrete ___Reinforeced with double layered Y16 deformed steel in both directions/use vibrator in accordance with specifications | Belethawa | M3 | 8.17
1.6 | Ground Beam Excavation: Excavate (0.5x0.4x35.4)m foundation, level and compact well ( before receiving foundation blinding)/cut and trim all projected faces | Belethawa | M3 | 7.08
1.7 | Beam Blinding: Lay 50mm thick lean (0.5x0.1x35.4)m concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size as Perspecification above the excavated footing and foundation trenchs, cure the blinding | Belethawa | M3 | 1.77
1.8 | Ground TIE Beams: provide and cast (0.4x0.45x35.4m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y14 linked with Y8mm stirupps @200mm c/c | Belethawa | M3 | 6.37
1.9 | Backfilling with Good Hardcore and Crashed Stone: supply and fill (imported or Excavated selected material over the ground floor compact AS PER Specification | Belethawa | M3 | 7.08
| SUBTOTAL |  |  |  |  | 0
2 | SUPER- STRUCTURE
2.1 | Middle Tie Beams: provide and cast 2x(0.4x0.4x41.4m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y14 linked with Y8mm stirupps @200mm c/c | Belethawa | M3 | 6.62
2.2 | Bottom Slab: Cast in place (200x4000x5000)mmThick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | Belethawa | M3 | 4
2.3 | Slab Beam: provide and cast (0.4x3.8x4.8m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y16 linked with Y8mm stirupps @200mm c/c | Belethawa | M3 | 18.24
2.4 | Columns: Cast in place 9(0.4x0.4x8.05)m R.C.C Columns Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with 6Y16mm +R8@150mm c/c | Belethawa | M3 | 11.59
2.5 | Base of Roof Slabs: Cast in place (150x4000x5000)mm Thick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | Belethawa | M3 | 3
2.6 | RCC WALLS: provide and cast (200x1500x18)MM RCC Wall MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with Y10 linked with Y8mm stirupps @200mm c/c | Belethawa | M3 | 5.4
2.7 | Wall Plaster: apply No 2 coats of 20mm thick plastering Mix 1:4 to intenal external walls including seiving sand and even finish as per line in levels , curing as per Field Engineer | Belethawa | M2 | 10.8
2.8 | White Washing : apply No2 coats of white washing to all int.and external walls | Belethawa | M2 | 10.8
2.9 | Emulsion paint: apply No2 coats of emulsion paint to all int.and external walls except where stone facing is used | Belethawa | M2 | 10.8
2.1 | Manhole For during Cleaning:Provide (600mmx600mm) RCC Roof Access cover Cleaning in a future | Belethawa | LMS | 1
2.11 | Roof Slabs: Cast in place (150x4000x5000)MM Thick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | Belethawa | M3 | 3
2.12 | G.I pipe :Provide and install inlet pipe & over flow pipe | Belethawa | PCs | 3
2.13 | provide and fix steel ladder for elevated Tank | Belethawa | PCs | 1
2.14 | Provide and install Cleaning Pipe | Belethawa | PCs | 1
| SUBTOTAL |  |  |  |  | 0
GRAND TOTAL FOR CONSTRUCTION OF 30M3 ELEVATED WATER TANK IN USD
B | CONSTRUCTION OF NEW WATER KIOKS WITH CHAIN LINK FENCE
S.No | DESCRIPTIONS OF WORK/ACTIVITIES |  | UNIT | QUANTITY | Unit Price (USD) | Total Price (USD)
| CONSTRUCTION OF WATER KIOSKS | Belethawa
1.1 | Site clearance: leveling and clear unnecessary materials | Belethawa | M2 | 6.7
1.2 | Excavation foundation trench and level (2.4m x 2.8 x0.4 )x2 | Belethawa | M3 | 5.4
1.3 | Mass concrete of 50mm thick blinding layer (1:2:4 mix) under the foundation wall 2.4m x 2.8 x0.05) | Belethawa | M3 | 0.336
1.4 | 250mm hardcore filling and well compacting for slab area(2.4mx2.8m) | Belethawa | M2 | 6.72
1.5 | RC concrete (1:2:4 mix ) in conc. floor slab 15 cm thick(2.4mx2.8mx0.15m) | Belethawa | M3 | 1.008
1.6 | 40cm thick masonry block walling in cement & sand mortar 1;3 mix () | Belethawa | M3 | 1.152
1.7 | Construct 200mm block bended with mix ratio of 1:4cement/sand (1.6mx0.6m) | Belethawa | M2 | 0.96
1.8 | Cast 20cm Mass concrete 1:3:6 mix design of the area (1.6x0.2x0.2m) | Belethawa | M3 | 0.064
1.9 | External & internal plastering ,12 mm thick, cement and sand mix 1:4, with wood float finish. | Belethawa | M2 | 6.2
1.1 | Apply two coats of white wash and destempering | Belethawa | M2 | 6.2
1.11 | 30 mm thick 1:3 cement/sand floor screed | Belethawa | M3 | 6.72
1.12 | GI pipes for water Kiosk 1'' | Belethawa | Pcs | 4
1.13 | Construct Complete drainage water collection with 1000mm dia for water kiosk(Soak Pit)(1500x1500x1200)mm, cover Precast concrete and fill gravel | Belethawa | M3 | 1.5
2 | Fittings on the kiosk | Belethawa
2.1 | GI Reducer 2" -1" | Belethawa | Pcs | 1
2.2 | 900 GI Elbow 1" | Belethawa | Pcs | 2
2.3 | 1" GI Double Tee | Belethawa | Pcs | 2
2.4 | 1" GI Single Tee | Belethawa | Pcs | 1
2.5 | Reducer socket 1"-3/4" | Belethawa | Pcs | 6
2.6 | Nipple GI | Belethawa | Pcs | 6
2.7 | Branch pipes, 3/4", galvanized (long pipe 300mm threaded on both sides ) | Belethawa | Pcs | 6
2.8 | G.I 3/4" taps | Belethawa | No | 6
2.9 | Supply and install the water point Water Fow Meter,Awakingdemi 15mm 1/2 inch Water Meter Read of Cubic Meters for Water kiosk Using with Fittings and keep protect position See the design position | Belethawa | No | 1
2.1 | Supply and construct of chain fencing of the communal water points with GI pipe 2.5" dia. B-class and 2m clear height every 2 meter length and the chain link is 50mmx50mm opening and 2.7mm dim. Price includes digging for foundation, concrete foundation works, supply and erection of corner posts at bend points, intermediate posts, mesh wire, 4mm galvanized mild steel straining wires, etc... complete as per the detailed drawings for the fencing. The cost also includes painting work. All material shall be approved my site engineer 30mx2m(LxW) . | Belethawa | ML | 60
2.2 | Supply and Fix 7" of Angular for as a Columns Fixing the ground | Belethawa | PCs | 20
2.3 | Construction Footing and Blinding to fix G.I Pipe, then to 30cm above the footing, and welden the Security net into G.I And fix Two sides frame door of 1.5mx1.8m | Belethawa | No | 12
2.4 | Construction foundation of Marble stone and concrete above the foundation a Ground beam Lean concrete to fix the Chain Link fence 40cm above the ground floor and insert the 10cm the chain link in to the footing above the ground(20cx0.2x0.40) | Belethawa | M3 | 1.6
TOTAL COST IN USD FOR 1 NEW WATER KIOSKS
| GRAND TOTAL COST FOR 1 NEW WATER KIOKS |  |  |  | 1 | 0
C | DISTRIBUTION OF NEW PIPELINE EXTENSION FROM ELEVATED TANK TO THE NEW WATER KIOSKS THE PIPE LENGTH 8KM
ITEM | DESCRIPTION |  | UNIT | QTY | Unit Price (USD) | Total Price (USD)
PIPELINE EXCAVATION
1 | Trenching, laying and backfilling of pipeline (for 75mm or 3”Inch Pvc High Pressure pipe Class D) for internal distribution system (450mm x 600mm trench) from shallow well to new elevated tank. | Belethawa | LM | 8000
3 | PIPELINE SUPPLIES AND INSTALLATION
4 | HDPE pipe 3-inch diameter PN 16 , including all its connectors (75mm pipe) (100m long).Prosed for direct supply from water source to storage tank, | Belethawa | Rolls | 80
5 | HDPE pipe 2-inch diameter PN 10 including all its connectors (50mm pipe) (100m long) prposed for internal distribution from tank to water kioks | Belethawa | Rolls | 1
6 | 75mm HDPE TEE(FUSION) | Belethawa | Pcs | 1
7 | 75MM HDPE GET VALVE (FUSION) | Belethawa | Pcs | 1
8 | Assorted Pipe fittings (Tap + valve,cap + union+reducer+ Elbow +stop cack & Solvent Glue) | Belethawa | Nr | 1
9 | 2½-inch (DN65) Non-Return Valve (NRV) suitable for HDPE PN16 pipeline systems: | Belethawa | Nr | 4
10 | Cost for plumbing works for pipeline | Belethawa | LS | 1
11 | TOTAL FOR 8KM PIPELINE EXTENSIONS |  |  |  |  | 0
Item | DESCRIPTION |  | UNIT | QTY | Unit Price (USD) | Total Price (USD)
D | Shallow Well Rehabilitation and Excavation additional 5m in Depth
2.1 | Pumping out water from the well and do Diselting sand cleaning all ud and rubish materials from the well | Belethawa | M3 | 1
| Excavate and deepen an additional of 5m Depth for the shallow well, prepare precasting RRC rings install properly to the additional dimensions. | Belethawa | M3 | 3.927
2.2 | Construct a concrete masonry apron of 1m high circular foundation and construct 100mm cover slab at the top of the well and install a 400mm2 steel door for maitenance use. | Belethawa | M3 | 3.14
2.3 | Gravel Packing:Provide cleaned and washed gravel and packing at the bottom of the well to conduct filtration admixture,15mm thick rendering | Belethawa | M3 | 1
2.4 | Procure and install Submersible pump, PS2 1800 Lorentz-3kw, with matching cut-off electrodes, drop cables control panel, all accessories included (Stand by Pump) | Belethawa | PCs | 1
2.5 | Supply and Install 2.5 inch PVC Pipe for submersible pump and connect to main pipe | Belethawa | PC | 8
2.6 | T-joint | Belethawa | PC | 15
2.7 | G-Valve(2 inch) | Belethawa | PC | 6
2.8 | Elbo- | Belethawa | PC | 20
2.9 | Valve socket | Belethawa | PC | 8
3 | Glue fax | Belethawa | kg | 10
3.1 | Return valve(2inch) | Belethawa | PC | 3
4 | CONSTRUCTION OF CHAIN LINK FENCE
4.1 | Provide materials and construction of chain Link Fence made from GI pipe 2.5" dia. B-class and 1.8m clear height every 2.5 meter length, The chain link is 50mmx50mm opening and 2.7mm dim. | Belethawa
4.2 | Supply and install the chain link is 50mmx50mm opening and 2.7mm dim. Which the roll is 30mx2m(LxW) | Belethawa | roll | 3
| • Area of Solar Panels: | Belethawa
| • Width: 992x12=11,904mm | Belethawa
| • Length: 1956x8=15,648mm | Belethawa
4.3 | Supply and fix 5" of angular for as a columns fixing the ground | Belethawa | pcs | 35
4.5 | Construction footing and blinding to fix GI pipe, then 50cm above the footing, and welding the security net into GI and fix two frame door of 1.5mx2m, and 3mx2m | Belethawa | ea | 35
4.6 | Construction foundation of marble stone and concrete above the foundation a ground beam Lean concrete to fix the Chain Link fence 40cm above the ground floor and insert the 10cm the chain link in to the footing above the ground(120x0.40x0.40) | Belethawa | m3 | 19.2
4.7 | Supply and install wires fixing above the chainlink but on the welding GI angular and fence net | Belethawa | roll | 15
4.9 | SUBTOTAL IN USD FOR SHALLOW WELL REHABILITATION
E | SOLAR INSTALLATION AND FENCING
| DESCRIPTION |  | UNIT | QTY | Unit Price (USD) | Total Price (USD)
1.1 | Supply and Install Solar Panels and Accessories of Mono Crystalline with following specification -Solar panels 595watt jinko branding | Belethawa | No | 28
| • Type ………………………………………......................595 – 72M •Peak Power (Pmax) ………………............................595 W • Open Circuit Voltage (Voc) …………............................50.1 V • Short Circuit Current (Isc) …………............................14.2 A •Max. Power Voltage (Vmp) …………............................41.9 V • Max. Power Current (Imp) …………............................13.6 A • Maximum System Voltage…………......…................... 1500 V • Power Tolerance:……………………..……...................+/- 3% •Dimensions (mm) ………………………....…............... 2278 × 1134 × 35 Note: All technical data measured under Standard Test Conditions (STC):AM = 1.5, E = 1000 W/m², Tc = 25 °C. | Belethawa
1.2 | Suply and Install stainless steel Solar Pump Inverter of RS10100-3L-0012-4-X+HMGR 10KW or equivalent submersible pump (DC/AC Inverters Grundfox) Controller/ pump Inverter Input U1:3AC 380-480V 50/60Hz, 11:11.3A DC 400-800V, Output 3 0-Input V 0-320Hz, 12:12A, Power P2: 5.5kw, 400V/7.5Hp:380V IP66 AC. • working temperature: -10～+50℃ • Well sensor. • Water Tank sensor. | Belethawa | No | 1
1.3 | DC Wire for Special solar cable - 40 ～+1250C Max 1000V AC/1800V DC 1x6.0 mm2 | Belethawa | Meter | 300
1.4 | Combiner fuse box & small accessory • DC Combiner Fuse box • DC circuit breaker • Manual transfer switch-generator & PV Array of 100A max | Belethawa | No | 1
1.5 | Case Water Proof for Solar pump inverter | Belethawa | PCs | 1
1.6 | Supply and install CABLE 3 core, 3x10 mm2 | Belethawa | Meter | 120
1.7 | Installation, internal wiring sundries, sensors. | Belethawa | LMS | 1
1.8 | Supply and Install the Solar Ground Mounting of Golvanized Steel Ranking Structure frame with Gentel sloping of 1.6m Elevation ,1.4m@<150 and Sett off the resistance of the air space of 2mm,Bolding and welding the frame work Fix to the footing | Belethawa | Kw | 3
1.9 | • Excavation Footing (600x500x500) • Reinforced concrete to bellow the ground (600x500x500) bellow the ground and • Reinforced Concrete Above the ground (500x500x500)mm above the ground with base of • Supply and fix 3 Inch Galvanized steel Pipe Class B for Columns • Supply and Fix mounting of Galvanized Steel Ranking Structure • Man powering, unti rust painting with a ranking frame of Serial and Parallel as you see the attached Drawing with a technical guidance of Engineer for 11,250Wp | Belethawa | Unit | 1
SUB TOTAL COST IN USD
SOLAR FENCING
| Provide materials and construction of chain Link Fence made from GI pipe 2.5" dia. B-class and 1.8m clear height every 2.5 meter length, The chain link is 50mmx50mm opening and 2.7mm dim. | Belethawa
1 | Supply and Install The chain link is 50mmx50mm opening and 2.7mm dim. Which the roll is 30mx2m(LxW) The • Area of Solar Panels: • Width: 992x12=11,904mm • Length: 1956x8=15,648mm | Belethawa | Roll | 4
2 | Supply and Fix 5" of Angular for as a Columns Fixing the ground | Belethawa | PCs | 35
3 | Construction Footing and Blinding to fix G.I Pipe ;the n to 50cm above the footing, and welden the Security net in to G.I And fix Two frame door of 1.5mx2m, and 3mx2m | Belethawa | No | 35
4 | Construction foundation of Marble stone and concrete above the foundation a Ground beam Lean concrete to fix the Chain Link fence 40cm above the ground floor and insert the 10cm the chain link in to the footing above the ground(120cx0.40x0.40) | Belethawa | M3 | 19.2
5 | Supply and install Wires Fixing above the chainlink but on the weldening G.I Angular and Fence Net | Belethawa | Roll | 15
SUB TOTAL COST IN USD
GRAND TOTAL USD FOR SOLAR INSTALLATION AND FENCING
ITEM | DESCRIPTION |  | UNIT | QTY. | Unit Price (USD) | Total Price (USD)
COST SUMMARY FOR BXW- SHALLOW WELL REHAB
1 | GRAND TOTAL FOR CONSTRUCTION OF 30M3 ELEVATED WATER TANK IN USD | Belethawa | Lumpsum | 1
2 | SHALLOW WELL REHABILITATION | Belethawa | Lumpsum | 1
3 | TOTAL FOR 8KM PIPELINE EXTENSIONS | Belethawa | Lumpsum | 1
4 | GRAND TOTAL FOR 1 NEW WATER KIOSKS | Belethawa | Lumpsum | 1
5 | GRAND TOTAL USD FOR SOLAR INSTALLATION AND FENCING | Belethawa | Lumpsum | 1
6 | GRAND TOTAL FOR BELEDHAWA SHALLOW WELL REHAB |  | Lumpsum
GPS Coordinate for Allongo proposed shallow well Rehab
No. | Infrastructure Type |  | Site Name / Location | Latitude (N) | Longitude (E) | Elevation (m)
1 | Bore hole/ shallow well | Belethawa | ALONGO | 4.004 | 41.9385 | 185.69-+9.0m
2 | water tank | Belethawa | ALONGO | 3.9711 | 41.991 | 221.11-+3.2m
3 | water kioks 1 | Belethawa | ALONGO | 3.9711 | 41.991 | 206.08-+5.69m
6 | pipeline extension | Belethawa | ALONGO | 4.004033, 41.938508 | 3.971072, 41.990991
7 | solar installation | Belethawa | ALONGO | 4.004 | 41.9385 | 185.69+9.0m
DRC to complete |  |  |  | Bidder to complete
Delivery time required (days after PO signature): |  | DRC Expects the Works to be Completed within 60 Calendar Days |  | Delivery time offered (days after PO signature):
Delivery Terms required (Add Incoterm if necessary): |  | DDP |  | Delivery Terms offered (must include incoterm):
Delivery Destination required: |  | Belethawa (Alongo Village Camp in Belethawa) |  | Delivery Destination offered:
Minimum bid validity period required: |  | 60 Days |  | Bid validity period offfered:
Additional comments to bidders: |  |  |  | Company Name:
Contact Person:
|  |  |  | Address: |  | Phone number:
|  |  |  | Email Address: |  | Date:
Signed by a duly authorized company representative:
Title:
Print Name:
Stamp of company