## GLK-BH-REHAB
BILL OF QUANTITIES FOR REHABILITATION OF HILMO BOREHOLE
S.No | DESCRIPTIONS OF WORK/ACTIVITIES | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
1.1 | Mobilization of the Crane to the Site with specification Capacity: 35-ton Boom length: 8.4 – 30.4-meter main boom + 8 – 15-meter fly jib with hydraulic offset | Unit | 1 |  | 0
1.2 | Re-move the old existing system, Supply and Installation of PVC Pipes Supply and install 3-inch PVC pipes suitable for submersible pump applications, complete with all required accessories and fittings. Pipe Specifications: Material: High-quality PVC (uPVC) Nominal Diameter: 3 inch Standard Length: 6 meters per pipe Quantity: 12 pieces Pressure Rating: Suitable for high-head submersible pump discharge Application: Water conveyance / pump discharge line Joint Type: Solvent cement / rubber ring joints as per manufacturer recommendation Installation: Proper alignment, support, and leak-proof jointing | Unit | 1 |  | 0
1.3 | Submersible Pump (Revised Capacity) Supply and install one (1) submersible pump with the following characteristics: Power Rating: 7.5 kW (10 HP) Discharge Capacity: 14 m³/hour Total Dynamic Head: 150 meters Power Supply: 380 VAC, 3 Phase, 50 Hz Application: Borehole / deep well water pumping Complete with all standard accessories required for proper operation | PCs | 1 |  | 0
1.4 | upply Das GT-Sortiment GT-2 (GT-2 Glue) or approved equivalent, suitable for use with cables and fittings in water pump installations. | PCs | 2 |  | 0
1.5 | Supply and install applicable Control Panel Supply, install, and commission a suitable control panel for the submersible pump with the following requirements: Electrical Output: 380 VAC, 3 Phase, 50 Hz Compatibility: Specifically matched to the installed 7.5 kW (10 HP) submersible Protection Features: Overload, short circuit, phase failure, and dry-run protection Installation: Fixed at a suitable, accessible, and protected location Commissioning: Installation and testing to be carried out under the technical guidance of a qualified Engineer | PCs | 1 |  | 0
1.6 | Supply and Install Dual core of 150m of PVC Insulated Cables of 3x16mm2 | M | 150 |  | 0
Total for Borehole Rehab |  |  |  |  | 0
BILL OF QUANTITIES FOR BOREHOLE SOLARIZATION
#NAME? | DESCRIPTIONS OF WORK/ACTIVITIES | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
1
Note: Solar Rehabilitation of solar power system upgrading in shine Water Source system at Baidoa depth
1.1 | Supply and Install Solar Panels and Accessories of Mono Crystalline Type No. 20 PCs which is CERTIFIED M2 SOLAR Producted by International Organization for Standardization(ISO) and the Efficiency between 17 - 24%// Supply and Install erect solar panel Mountain/Ranking structure made of Stainless steal of 8790w or aproximately 15 kw • Type ………………………………………......................450 – 78M • Peak Power (Pmax):……………………........................450 W • Open Circuit Voltage (Voc)…………............................ 54.5+/-3% V • Short Circuit Current (Isc)……………........................... 10.71+/-5% A • Max.Power Voltage (Vmp)…………............................. 44.3 V • Max.Power Current (Imp)……………............................10.16 A • Maximum System Voltage…………......…................... 1000/1500 V • Power Tolerance:……………………..……...................+/- 3% • Dimensions (MM)……………………....….....................2180 x 996 x 35mm Note: All Technical Data at a Standard test Condition AM=1.5, E=1000 W/M2, Tc=25 C0 | No | 20 |  | 0
1.2 | Suply and Install stainless steel Solar Pump Inverter controler GD100-7R5G-4-PV Rated pawer Output 7.5KW or equivalent submersible pump (DC/AC Inverter) Controller/ pump Inverter Input U1:3AC 380-480V 50/60Hz, 11:11.3A DC 400-900V, Output 3 0-Input V 0-320Hz, 12:12A, Power P2: 18kw, 400V/7.5Hp:380V IP66 AC. • working temperature: -10～+60℃ • Well sensor. • Water Tank sensor. | PCs | 1 |  | 0
1.3 | Supply for Installation of system DC Wire for Special solar cable - 40 ～+1250C Max 1000V AC/1800V DC 1x6.0 mm2 | m | 200 |  | 0
1.4 | Combiner fuse box & small accessory • DC Combiner Fuse box • DC circuit breaker • Manual transfer switch-generator & PV Array of 100A max and PV disconnector | No | 1 |  | 0
1.5 | Case Water Proof for Solar pump inverter | pcs | 1 |  | 0
1.6 | Supply and install CABLE 4 core, 3x10 mm2 | m | 30 |  | 0
1.8 | Supply and Install the Solar Ground Mounting/Ranking structure of Golvanized Steel Ranking Structure frame with Gentel sloping of 1.6m Elevation ,1.4m@<150 and Sett off the resistance of the air space of 2mm,Bolding and welding the frame work Fix to the footing | Kw | 2.5 |  | 0
1.9 | • Excavation Footing (600x500x500) • Reinforced concrete to bellow the ground (600x500x500) bellow the ground and • Reinforced Concrete Above the ground (500x500x500)mm above the ground with base of • Supply and fix 3 Inch Galvanized steel Pipe Class B for Columns • Supply and Fix mounting of Galvanized Steel Ranking Structure • Man powering, unti rust painting with a ranking frame of Serial and Parallel as you see the attached Drawing with a technical guidance of Engineer for 11,250Wp | Unit | 1 |  | 0
SUBTOTAL IN USD |  |  |  |  | 0
CONSTRUCTION OF CHAIN LINK FENCE
Note:
Provide materials and construction of chain Link Fence made from GI pipe 2.5" dia. B-class and 1.8m clear height every 2.5 meter length, The chain link is 50mmx50mm opening and 2.7mm dim.
1 | Supply and Install The chain link is 50mmx50mm opening and 2.7mm dim. Which the roll is 30mx2m(LxW) The • Area of Solar Panels: • Width: 996x12=11,904mm • Length: 2180x8=15,648mm | Roll | 4 |  | 0
2 | Supply and Fix 5" of Angular for as a Columns Fixing the ground | PCs | 15 |  | 0
3 | Construction foundation of Marble stone and concrete above the foundation a Ground beam Lean concrete to fix the Chain Link fence 40cm above the ground floor and insert the 10cm the chain link in to the footing above the ground(150cx0.40x0.40) | M3 | 16 |  | 0
4 | Supply and install Wires Fixing above the chainlink but on the weldening G.I Angular and Fence Net | Roll | 15 |  | 0
SUBTOTAL IN USD |  |  |  |  | 0
GRAND TOTAL USD |  |  |  |  | 0
BILL OF QUANTITIES FOR CONSTRUCTION OF ELEVATED 30M3 WATER TANK
S.No | DESCRIPTIONS OF WORK/ACTIVITIES | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
CONSTRUCTION OF 30M3 ELEVATED TANK @12M Hight
Note:
The quantities are given is The Construction 30M3, 12M Hight. Quantities to be verified if these dimensions are varied
1 | SUB STRUCTURE
1.1 | Site clearance: clear site from vegetation, debris, unwanted material and despose it to a safe place | LMS | 1 |  | 0
1.2 | Footing Excavation: Excavate 9 (1.2x1.2x1.6)m Blind for footings, level and compact well ( before receiving foundation blinding)/cut and trim all projected faces | M3 | 20.74 |  | 0
1.3 | Hardcore: supply and fill 300mm 9(1.2x1.2x0.3) (imported or Excavated selected material over the ground floor compact AS PER Specification before recieving blinding | M3 | 3.89 |  | 0
1.4 | Foundation Blinding: Lay 50mm thick lean 4 (1.2x1.2X0.1)m concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size AS PER SPECSabove the excavated footing and foundation trenchs, cure the blinding | M3 | 1.296 |  | 0
1.5 | Footing concrete : provide and cast 9 (1.1x1.1x0.75)m R.C.C footing over the blinding mix 1:2:4 /6bags of cem/1cum of concrete ___Reinforeced with double layered Y16 deformed steel in both directions/use vibrator in accordance with specifications | M3 | 8.17 |  | 0
1.6 | Ground Beam Excavation: Excavate (0.5x0.4x35.4)m foundation, level and compact well ( before receiving foundation blinding)/cut and trim all projected faces | M3 | 7.08 |  | 0
1.7 | Beam Blinding: Lay 50mm thick lean (0.5x0.1x35.4)m concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size as Perspecification above the excavated footing and foundation trenchs, cure the blinding | M3 | 1.77 |  | 0
1.8 | Ground TIE Beams: provide and cast (0.4x0.45x35.4m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y14 linked with Y8mm stirupps @200mm c/c | M3 | 6.37 |  | 0
1.9 | Backfilling with Good Hardcore and Crashed Stone: supply and fill (imported or Excavated selected material over the ground floor compact AS PER Specification | M3 | 7.08 |  | 0
SUBTOTAL |  |  |  |  | 0
2 | SUPER- STRUCTURE
2.1 | Middle Tie Beams: provide and cast 2x(0.4x0.4x41.4m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y14 linked with Y8mm stirupps @200mm c/c | M3 | 6.62 |  | 0
2.2 | Bottom Slab: Cast in place (200x4000x5000)mmThick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | M3 | 4 |  | 0
2.3 | Slab Beam: provide and cast (0.4x3.8x4.8m) R.C.C beam MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with 4Y16 linked with Y8mm stirupps @200mm c/c | M3 | 18.24 |  | 0
2.4 | Columns: Cast in place 9(0.4x0.4x8.05)m R.C.C Columns Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with 6Y16mm +R8@150mm c/c | M3 | 11.59 |  | 0
2.5 | Base of Roof Slabs: Cast in place (150x4000x5000)mm Thick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | M3 | 3 |  | 0
2.6 | RCC WALLS: provide and cast (200x1500x18)MM RCC Wall MIX 1:2:4/6bags of cem/1cum of concrete___Reinforeced with Y10 linked with Y8mm stirupps @200mm c/c | M3 | 5.4 |  | 0
2.7 | Wall Plaster: apply No 2 coats of 20mm thick plastering Mix 1:4 to intenal external walls including seiving sand and even finish as per line in levels , curing as per Field Engineer | M2 | 10.8 |  | 0
2.8 | White Washing : apply No2 coats of white washing to all int.and external walls | M2 | 10.8 |  | 0
2.9 | Emulsion paint: apply No2 coats of emulsion paint to all int.and external walls except where stone facing is used | M2 | 10.8 |  | 0
2.1 | Manhole For during Cleaning:Provide (600mmx600mm) RCC Roof Access cover Cleaning in a future | LMS | 1 |  | 0
2.11 | Roof Slabs: Cast in place (150x4000x5000)MM Thick R.C.C Slab on the Water storage with Lid Mix 1:2:4/6bags of cem/1cum of concrete____Reinforced with Y12mm for Main bar & Y10 to Distribution +R8@150mm c/c | M3 | 3 |  | 0
2.12 | G.I pipe :Provide and install inlet pipe & over flow pipe | PCs | 3 |  | 0
2.13 | provide and fix steel ladder for elevated Tank | PCs | 1 |  | 0
2.14 | Provide and install Cleaning Pipe | PCs | 1 |  | 0
SUBTOTAL |  |  |  |  | 0
GRAND TOTAL FOR CONSTRUCTION OF 30M3 ELEVATED WATER TANK IN USD |  |  |  |  | 0
BILL OF QUANTITIES FOR 2.5 KM PIPELINE EXTENSION
S.No | DESCRIPTIONS OF WORK/ACTIVITIES | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
2 | Construction of 2.5 km Water Pipeline Extension Serving Alla Amin and Hayaan IDP Camps, Galkayo North and South Districts
Note: Construction, Excavation and Backfilling of 2500 m Pipeline extension and with a distribution of connection to the water points from the nearest point to the target IDP and Connect to water kiosks and at target IDP sites in Kahda from the main pipes from the nearest points guided by DRC Engineer at Targetting above Hayaan and Alla Amin IDP Camps at Galkacyo District
1 | DISTRIBUTION OF WATER PIPELINE AND INSTALLATIONS | M | 2500 |  | 0
Excavation of trench for piping 2500m (2.5 km) of length, depth 600mm, 400mm width from Water tank to the Water Point (kiosks) with a Backfilling and excavation of trench
2 | Supply and install of 2500m(2.5 km) of High Pressure 2 Inch 50mm Pvc Pipe For Water Supply From the nearest points and the distribution pipes to target IDP camp and connect 1 1/2 to the water points of a community access at a T-Junction with a supply of all fittings(Tap + valve,cap + union+reducer+ Elbow +stop cack & Plastic Glue) i.e | PCs | 40 |  | 0
GRAND TOTAL USD |  |  |  |  | 0
BILL OF QUANTITIES (BoQs) for Water Kiosk
S.No | DESCRIPTIONS OF WORK/ACTIVITIES | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
CONSTRUCTION OF WATER KIOSKS
Note:
BILL OF QUANTITIES FOR CONSTRUCTION OF WATER KIOKS
1 | Construction of water Kiosk
1.1 | Site clearance: leveling and clear unnecessary materials | M2 | 6.7 |  | 0
1.2 | Excavation foundation trench and level (2.4m x 2.8 x0.4 )x2 | M3 | 5.4 |  | 0
1.3 | Mass concrete of 50mm thick blinding layer (1:2:4 mix) under the foundation wall 2.4m x 2.8 x0.05) | M3 | 0.336 |  | 0
1.4 | 250mm hardcore filling and well compacting for slab area(2.4mx2.8m) | M2 | 6.72 |  | 0
1.5 | RC concrete (1:2:4 mix ) in conc. floor slab 15 cm thick(2.4mx2.8mx0.15m) | M3 | 1.008 |  | 0
1.6 | 40cm thick masonry block walling in cement & sand mortar 1;3 mix () | M3 | 1.152 |  | 0
1.7 | Construct 200mm block bended with mix ratio of 1:4cement/sand (1.6mx0.6m) | M2 | 0.96 |  | 0
1.8 | Cast 20cm Mass concrete 1:3:6 mix design of the area (1.6x0.2x0.2m) | M3 | 0.064 |  | 0
1.9 | External & internal plastering ,12 mm thick, cement and sand mix 1:4, with wood float finish. | M2 | 6.2 |  | 0
1.1 | Apply two coats of white wash and destempering | M2 | 6.2 |  | 0
1.11 | 30 mm thick 1:3 cement/sand floor screed | M3 | 6.72 |  | 0
1.12 | GI pipes for water Kiosk 1'' | Pcs | 4 |  | 0
1.13 | Construct Complete drainage water collection with 1000mm dia for water kiosk(Soak Pit)(1000x1500x1000)mm, cover Precast concrete and fill gravel | M3 | 1.5 |  | 0
2 | Fittings on the kiosk |  |  |  | 0
2.1 | GI Reducer 2" -1" | Pcs | 1 |  | 0
2.2 | 900 GI Elbow 1" | Pcs | 2 |  | 0
2.3 | 1" GI Double Tee | Pcs | 2 |  | 0
2.4 | 1" GI Single Tee | Pcs | 1 |  | 0
2.5 | Reducer socket 1"-3/4" | Pcs | 6 |  | 0
2.6 | Nipple GI | Pcs | 6 |  | 0
2.7 | Branch pipes, 3/4", galvanized (long pipe 300mm threaded on both sides ) | Pcs | 6 |  | 0
2.8 | G.I 3/4" taps | No | 6 |  | 0
2.9 | Supply and install the water point Water Fow Meter,Awakingdemi 15mm 1/2 inch Water Meter Read of Cubic Meters for Water kiosk Using with Fittings and keep protect position See the design position | No | 1 |  | 0
2 | CONSTRUCTION OF CHAIN LINK FENCE
Note:
Provide materials and construction of chain Link Fence made from GI pipe 2.5" dia. B-class and 1.8m clear height every 2.5 meter length, The chain link is 50mmx50mm opening and 2.7mm dim.
2.1 | Supply and Install The chain link is 50mmx50mm opening and 2.7mm dim. Which the roll is 30mx2m(LxW) The • Area of Solar Panels: Width: 992x12=11,904mm Length: 1956x8=15,648mm | ML | 2 |  | 0
2.2 | Supply and Fix 5" of Angular for as a Columns Fixing the ground | PCs | 8 |  | 0
2.3 | Construction Footing and Blinding to fix G.I Pipe, then to 30cm above the footing, and welden the Security net into G.I And fix Two sides frame door of 1.5mx1.8m | No | 12 |  | 0
2.4 | Construction foundation of Marble stone and concrete above the foundation a Ground beam Lean concrete to fix the Chain Link fence 40cm above the ground floor and insert the 10cm the chain link in to the footing above the ground(20cx0.2x0.40) | M3 | 1.6 |  | 0
SUBTOTAL FOR THE COST OF 1 WATER KIOSK |  |  |  |  | 0
GRAND TOTAL COST IN USD FOR CONSTRUCTION OF 3 WATER KIOSKS |  | 3 |  |  | 0
ANNEX 1: BILL OF QUANTITIES (BoQs) Summary
S.No | DESCRIPTIONS OF WORK/ACTIVITIES |  | UNIT | QUANTITY | Unit Cost (USD) | Total Cost (USD)
1 | Rehabilitation of Water source(Borehole) |  | No | 1 | 0 | 0
2 | Upgrading Solar power system Rehabilitation |  | No | 1 | 0 | 0
3 | Construction of 30M3 Elevated Water tank |  | No | 1 | 0 | 0
4 | 2.5KM Pipeline Extentions |  | No | 1 | 0 | 0
5 | Construction of Water kiosks |  | No | 3 | 0 | 0
| GRAND TOTAL USD FOR REHABILITATION OF HILMO WATER SOURCE AT GLK DISTRICT |  |  |  |  | 0
GPs coordinate
| Infrastructure Type | Site Name / Location |  |  | Latitude (N) | Longitude E
| Rehabilitation of Water source(Borehole) | Mudug_GLK_ South Hilmo Borhole |  |  | 6°17'7.58"N | 47°16'32.33"E
| Upgrading Solar power system Rehabilitation | Mudug_GLK_South Hilmo Borhole |  |  | 6°17'7.58"N | 47°16'32.33"E
| Construction of 30M3 Elevated Water tank | Mudug_GLK_South Hilmo Borhole |  |  | 6°17'7.58"N | 47°16'32.33"E
| 0.5KM Pipeline Extentions | Mudug_GLK_ South Har-Haar Borhole |  |  | 6.846392, | 47.4275
| 2 KM Pipeline Extentions | Mudug_GLK_North Alla Amin Borhole |  |  | 6.689605, | 47.4377