## construction of shallow well
ANNEX 1: BILL OF QUANTITIES (BoQs)
S.No | DESCRIPTIONS OF WORK/ACTIVITIES | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
1 | Shallow well construction (Dia 1.5) and Depth 13m at Warcadey Village In belet xawa District
Note: Solar Installation of Qurdubey Water infrastructructure Deeping well depth 13m, Static Water level 5m, Depth of Pump Installed/pump level 11m with a Pumping test, transport Provision of all required tools, equipment and construction materials and clearing of site upon arrival.
1 | Excavation including maintaining and supporting sides and keeping free from water, mud and fallen materials by bailing, pumping or otherwise | LS | 1
2 | Excavate a circular well shaft of 1.5 meters in diameter manually to a depth of 13 meters and dispose off the materials as will be directed by the engineer. Ensure the well walls are vertical, stable, and smooth to prevent collapse durin excavation | CM | 70.65
3 | Extra-over for excavation in soft rock | CM | 3
4 | Cart away and deposit surplus material as directed | CM | 18
5 | FILLING 400mm thick approved natural ground material,Well compacted approved selected material | CM | 25
6 | WELL LINING Vibrated Reinforced Concrete class 30(1:1:2) with 20mm thick maximum aggregate size in Well ring | CM | 0.471
7 | Installation Reinforced perforated concrete casing 1500mm diameter x 100mm wall thickness x 1000mm high up to 35m depth | No. | 22
| Concrete Rings: Prepare and install Pre-cast reinforced concrete (class 25) rings of 1.5m in diameter and 0.5m in height, with a wall thickness of 50mm. Reinforced with 6mm steel bars placed @ 150mm intervals, both horizontally and vertically. The price includes Grouting between rings using 1:3 sand-cement mortar mix | No. | 26
| Construct a 3m RC apron (1.5m below GL and 1.5m above GL) with a cast in situ Reinforced Concrete of a 1:2:3 ratio, using Vertically Y 10 spaced in 150mm and Horizontally Y8 bars spacing in 200mm, the price should include formworks and scaffolding | No. | 30
9 | Gravel Packing:Provide cleaned and washed gravel and packing at the bottom of the well to conduct filtration admixture,15mm thick rendering | LS | 1
10 | every one hour interval at least 36 continous hours) Water recharge testing(testing of the well using electrical submersible pump, the contractor to provide necessary power, etc and proper record | Item | 1
11 | Disinfection of well: Disinfect the well with a chlorine solution (50mg/L concentration) to kill any harmful bacteria or microorganisms before water is drawn for use | Item | 1
12 | Analysis of Water, using field test kits;2 water sample for each of the tests including Chemical, bacterial and Turbidity tests | Item | 1
SUB TOTAL COST IN USD
SUPPLY AND INSTALL SUBMERSIBLE PUMP AND MAIN RAISER PIPES
1 | Procure and install Submersible pump, PS2 1800 Lorentz-3kw, with matching cut-off electrodes, drop cables control panel, all accessories included (Stand by Pump) | PCs | 1
2 | Supply and Install 3 inch PVC Pipe for submersible pump and connect to Elevated tank | PC | 8
3 | T-joint | PC | 15
4 | G-Valve(2 inch) | PC | 6
5 | Elbo- | PC | 20
6 | Valve socket | PC | 8
7 | Glue fax | kg | 15
8 | Return valve(2inch) | PC | 4
9 | Excavation of the trunch of the water pipes 30mx0.3mx0.5m | cum | 7.5
SUB TOTAL COST IN USD |  |  |  |  | 0
GRAND TOTAL USD FOR ONE SHALLOW WELL |  |  |  |  | 0