## Final BOQ
Put your company logo here
Annex A: Bill of Quantity
Rehabilitation and Upgrading of Boreholes with Civil Works, Equipment, and Solarization
S/N | Description | Unit | Quantity | Rate (US$) | Amount (US$)
1 | Construction of water kiosk
1 | Clearance of the area | m2 | 16 |  | 0
2 | Construction of rublle stone- 300mm below ground level and 100mm above ground level. | m3 | 4 |  | 0
3 | Casting 200mm thick slab with R8 reinforcement at 300mm both ways (6x6x0.20)m | m3 | 7.1 |  | 0
4 | Construction of Reinforced Conrete stand with Y8 reinforced to make the strong enough to with stand water pressur | m2 | 1.5 |  | 0
5 | Plastering of walls both sides, inside with bure cement grout after plaster to prevent water leakage | m2 | 22 |  | 0
6 | emulsion Painting of water kiosk and logs(ACF and Doner log at least two visible sides of water kiosk) | m2 | 22 |  | 0
7 | Supply and fixing of water taps at least two side of water kiosk each 3 water taps. | Pieces | 6 |  | 0
Sub total of water kiosk |  |  |  |  | 0
2 | Reahbilitation of water tank
1 | Cement | Sacks of 50kg | 180 |  | 0
2 | sand | Load of 6 cubic meter | 11 |  | 0
3 | gravel | Load of 6 cubic meter | 1 |  | 0
4 | stone | Load of 6 cubic meter | 1 |  | 0
5 | Emulsion paint | Liter | 22 |  | 0
6 | Labour
7 | Mason (2) | Days | 13 |  | 0
8 | Carpentry/iron bender (1) | Days | 8 |  | 0
9 | Plumber (1) | Days | 2 |  | 0
10 | Foreman (1) | Days | 13 |  | 0
11 | Unskilled labour (6) | Days | 10 |  | 0
Sub total of water tank |  |  |  |  | 0
3 | Extesion of water pipeline from borehole to communities
1 | Excavation of pipeline at the depth of 70cm from borehole to community/water point 2950m long | m | 400 |  | 0
2 | Supply and laydown Pipe line(Single line PVC 3'', 2'' and 1'') High pressure pipe (Black one), all pipe fittings, back filling and labour. this also includes Pressure valves | m | 400 |  | 0
| Sub total of water pipeline |  |  |  | 0
4 | HYBRID SYSTEM
A | Resorce mobilization, demobilization, Site Clearing and excavation for column erection | L.sum | 1 |  | 0
B | Supply and Install Solar Panels of Mono Crystalline Type No. 60 PCs which is CERTIFIED M2 SOLAR Producted by International Organization for Standardization(ISO) and the Efficiency between 17 - 24% • Type ………………………………………....................... 350 – 72M • Peak Power (Pmax):……………………........................ 350 W • Open Circuit Voltage (Voc)…………........................... 47.7V • Short Circuit Current (Isc)……………......................... 9.42 A • Max.Power Voltage (Vmp)…………............................. 38.7 V • Max.Power Current (Imp)……………........................... 9.05 A • Maximum System Voltage…………......…................... 1000 V • Power Tolerance:……………………..…….................... +/- 3% • Dimensions (MM)……………………....…..................... 1960 x 990 x 40 Note: All Technical Data at a Standard test Condition AM=1.5, E=1000 W/M2, TC=25 C0 | No | 60 |  | 0
C | Supply stainless steel Solar Pump Inverter 15KW of (DC/AC Inverters With GPRS Romote Control) Controller/ pump Inverter Output 3PH 50Hz 0.440VAC, 15Kw, 32A, 0.400Hz & In put 350VDC to 800VDC or 380/440VAC • working temperature: -10～+50℃ • Well sensor. • Water Tank sensor. | No | 1 |  | 0
D | Submersible pump 50Hz 7.5KW 10HP Model KFT 4SP14-25 | Pieces | 1 |  | 0
E | Supply and Install DC Wire for Special solar cable - 40 ～+1250C Max 1000V AC/1800V DC 1x6.0 mm2 | M | 300 |  | 0
F | Combiner fuse box & small accessory • DC Combiner Fuse box • DC circuit breaker • Manual transfer switch-generator & PV Array of 100A max | No | 1 |  | 0
G | Case Water Proof for Solar pump inverter | No | 1 |  | 0
H | Cable 16mm x 4 core PVC insulated | M | 20 |  | 0
| Steel structure for solar panel support | lumpsum | 1 |  | 0
I | Installation, internal wiring sundries, sensors. | LMS | 1 |  | 0
R | Supply and Install Earthing and Elecical grounding use metallic rod (diameter = 25mm (1inch) and length = 2m (6ft) instead of earth plate for earthing system. The metallic pipe should be 2 meter below from the surface of ground. To maintain the moister condition, put 25mm (1inch) coal and Salt mixture around the earth plate | No | 1 |  | 0
S | Supply and installation of (30KVA, computed on basis of pump power requirement) Generator (Perkins generator set or equivalent approved meeting the following minimum specifications: - diesel driven, 3 phase, water cooled, dual staring with alternator and complete with 10 spare oil filters, 10 spare fuel filters and 2 spare air filters) | Pieces | 1 |  | 0
| Sub total of HYBRID SYSTEM |  |  |  | 0
| Total for one Borehole |  |  |  | 0
| Number of Boreholes |  |  |  | 2
Grand Total |  |  |  |  | 0
Name and Surname: (…………………………………………………………………….)
Duly authorized to sign this tender on behalf of: (.......................................................................)
Place, date and stamp: (……………………………………………………………………)