## Durdur Borehole
Rehabilitation of Durdur Borehole with Solar pumping system, submersible pump, Two water Kiosk, 1000m pipeline extension and 40m x 40m Fencing
BOREHOLE SOLAR WATER PUMPING SYSTEM WITH SUBMERSIBLE PUMP and PUMP TESTING
S/N | Item description | Unit | Quantity | Unit price | Total
1 | Supply and Install ongrid Solar pump Inverter of 20kw Grundfos or it's Lorentz equivalent. with all other accessories needed to use solar panels and ongrid power together. | Item | 1 |  | 0
2 | Supply and Install additional Solar panel same as the 28 panels installed there, Teir 1 -2 brands of monocrystalline 445WP, VoC 49.71V, Isc 9.9A, Vmp 42.4V, Imp 9.43A efficiency 15% efficiency, 1500V system voltage with 72series cells arrangement. (14 panels in series and 2 in parallel). | Nr | 40 |  | 0
3 | Supply and install AC cable 4cx16sqmm PVC insulated and UV Resistant with 2 splicing kits and 1 box of 50cm adhesive cable clips | m | 150 |  | 0
4 | Supply and install PVC DC Wire double core for solar 1x6mm black with cable connectors. | m | 80 |  | 0
5 | Manual change-over switch for 20kw Inverter, preferably 400Amp | pc | 1 |  | 0
6 | Surge Protector | Unit | 1 |  | 0
7 | PV Combiner 1000V_125A_4 ways | Unit | 1 |  | 0
8 | Supply and installation of Earthing Wire 6sqmm | m | 50 |  | 0
9 | Water meter 3" for borehole pipe. | Unit | 1 |  | 0
10 | Electric Float switch connected to the solar system. | Unit | 1 |  | 0
11 | Mounting Structure (Supply and construction of Aluminium module support structure and Concrete Foundation for Solar Panels of required high (according to the site requirements and supervisor Engineer instructions) The structure will be made of square hollow Aluminium anchored to the RC base in 800 mm deep hole 500 mm diameter.). | Unit | 1 |  | 0
12 | Accessories and Installation, Testing and Commissioning of solar system and training the operator with basic needed knowledge. | Lot | 1 |  | 0
13 | Provide and install a Submersible pump full set(15Kw, 150m head, 25m3/h discharge, Motor version T40, Class IP68, 2900rmp speed, 6inch motor diameter with outlet of 2 1/2 inches). - Grundfos or it's Lorentz equivalent. The cost should include the withdrawal of the old pump and riser mains with plumbing works. | Pc | 1 |  | 0
14 | Conducting Pumping and Recovery Test for the borehole. 1. Determining the well's sustainable pumping rate. 2. Assessing the static water level. 3. Assessing the recovery time. 4. Evaluating the suitability of the existing pump or selecting a suitable pump based on test results. | Lsm | 1 |  | 0
TOTAL BOREHOLE SOLAR WATER PUMPING SYSTEM WITH SUBMERSIBLE PUMP |  |  |  |  | 0
Note: There are 28 sollar panels of 445 watts, there will be a mounting structure and new 28 pannels of 445 watts and connected together.
CONSTRUCTION OF OPEN WATER KIOSK WITH 6 FAUCETS.
ITEM | ITEM DESCRIPTION | UNIT | Qty | RATE | AMOUNT
Excavation and Earthwork
1 | Excavate in soft material for foundation trenches not exceeding 250mm deep starting from stripped level | m3 | 2.4 |  | 0
| construction of water kiosk foundation using 200mm concrete hollow blocks with Cement mortar 1:6 (1 cement :6 coarse sand). | m2 | 5 |  | 0
Selected filling
2 | 250mm Thick hardcore filling compacted in layers not exceeding 150mm deep and well watered. | m3 | 2.4 |  | 0
3 | 50mm Thick quarry dust blinding to surfaces of hardcore (Measured Separately) | m2 | 0.5 |  | 0
Concrete work and Construction
Plain Concrete Class 15 / (1:3:6)
4 | 50 mm Thick slab on top of the laid hardcore. | m3 | 6 |  | 0
5 | 50mm thick concrete apron and drain channel | m3 | 1.7 |  | 0
6 | Construction of water kiosk wall using 200mm concrete hollow blocks with Cement mortar 1:6 (1 cement :6 coarse sand). | m2 | 5.5 |  | 0
Vibrated reinforced concrete class 25/20 with minimum cube crushing strength of 25N/mm² at 28 days
7 | 200mm 20/20 (1:2:4) RCC Capping. | m³ | 0.1 |  | 0
Mesh reinforcement ; B.S. 4483 ref A142 weighing 2.22 kgs per square meter including bends, tying wire and spacing blocks
8 | Fabric mesh reinforcement to ground floor slab | m2 | 12 |  | 0
Finishes
9 | Plaster (to wall, floor, etc) with cement and sand (1:6) mortar including rounding off or chamfering corners as directed and raking out joints including throating, nosing and drip course. | m² | 13 |  | 0
10 | Finishing wall with 100%Premium acrylic emulsion paint of approved brand and manufacture on wall surface, content including scraping and preparing the surface thoroughly, removing of dust etc all complete as permanufacturer's specification and direction of the site engineer. | m² | 13 |  | 0
Piping System
Supply, laying, test and commission the following:- PIPEWORK AND FITTINGS including All Joint Pipe Fittings all as required in the pipework installation. (elbows, nipples, sockets, gate valves, reducers, Tee PVC pipes, etc.)
11 | Excavate trench in all materials include for joint holes, trimming sides and preparing trench bottom, backfill with part of the materials and compact. Depth of excavation 0.5m and width not less than 0.4mm. | m³ | 3 |  | 0
12 | Backfilling either with insitu material or imported selected granular material for pipe surrounds and bedding as specified by the engineer. | m³ | 3 |  | 0
13 | 2 inch UPVC Pipe (High Preasure Pipe) Class C | m | 20 |  | 0
14 | Ditto but 1 inch | m | 12 |  | 0
15 | Taps 1" peglar | Nr | 6 |  | 0
16 | Gate valve 1" | Nr | 2 |  | 0
Soak away pit:
17 | Excavate (1000mm Diameter and 1500mm depth) soak pit, fill with granular material with high absorption capacity as shown in the drawing. | m3 | 1.2 |  | 0
Vibrated reinforced concrete class 25/20 with minimum cube crushing strength of 25N/mm² at 28 days
18 | 1100mm dia 75mm thick (1:2:4) soak pit cover slab. | No | 1 |  | 0
19 | Visibility board | Item | 1 |  | 0
TOTAL FOR CONSTRUCTION OF ONE WATER KIOSK |  |  |  |  | 0
TOTAL FOR CONSTRUCTION OF ONE WATER KIOSK |  |  |  | 2 | 0
1000m EXTENSION PIPE TO WATER KIOSK
ITEM | ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | EARTHWORKS
1.1 | Excavate trench in all materials include for joint holes, trimming sides and preparing trench bottom, backfill with part of the materials and compact. Depth of excavation 0.6m and width not less than 0.5m. | m³ | 300 |  | 0
1.2 | Backfilling either with insitu material or imported selected granular material for pipe surrounds and bedding as specified by the engineer. | m³ | 300 |  | 0
| SUBTOTAL 1 |  |  |  | 0
2 | PIPE WORK - PIPES
Supply, laying, test and commission the following:- PIPEWORK AND FITTINGS including All Joint Pipe Fittings all as required in the pipework installation. (elbows, nipples, sockets, gate valves, reducers, Tee PVC pipes, etc.)
2.1 | 2 inch UPVC Pipe (High Preasure Pipe) Class C | m | 1000 |  | 0
| SUBTOTAL 2 |  |  |  | 0
TOTAL OF 1000m EXTENSION PIPE TO WATER KIOSK |  |  |  |  | 0
FENCING OF 40mx40m
ITEM | ITEM DESCRIPTION | UNIT | QUANTITY | RATE [USD] | AMOUNT [USD]
1 | Excavate 400mm width and 400mm deep holes to receive 70 reinforced concrete posts to be spaced at 3.3m c/c | m³ | 11.2 |  | 0
| Supply and construct 3 layers of hollow blocks concrete for flood protecting along the perimeter of the fence, then plastering and painting it. | m² | 96 |  | 0
2 | Cast the excavated holes with reinforced concrete 1:2:4 mix with R10 reinforcement to receive 70 reinforced concrete posts. | m³ | 11.2 |  | 0
3 | Reinforced concrete posts cast minimum 450mm to ground in concrete surround 1:2:4 mix, 2.7m above ground with chamfer bend at top 40cm long with nail size holes done through 7 No. (spaced at 3m c/c) | No. | 54 |  | 0
4 | Ditto but diagonal members to support at the four corners. | No. | 16 |  | 0
5 | Supply and fix G16 Galvanized Razor Wire. including straining to allowable limit and fixing to reinforced concrete posts. | m | 160 |  | 0
6 | Supply and fix 3 mm thick straining wires in 4 strands including straining to allowable limit and fixing to reinforced concrete posts. | m | 640 |  | 0
7 | Allow for supply and fixing of G16 chain link 2.5m high well fixed to reinforced concrete posts to approval. | m | 160 |  | 0
8 | Provide materials and erect a steel gate with pedestrian gate size 3.5mx 3m high, comprising of 75x75x3 mm SHS framing and horizontal intermediate framing,50x50x3 mm SHS in vertical members at 150 mm centres,400mm x400mm reinforced concrete side poles fixed in ground with base reinforced concrete 1:2:4 mix complete with locking mechanism. | No. | 1 |  | 0
9 | Providing & fixing of permanent information sign board after the completion of the project as per the instruction of the Project Engineer. | Lsm | 1 |  | 0
TOTAL OF FENCING 40M X 40M |  |  |  |  | 0
GRAND TOTAL OF DUDRDUR BOREHOLE |  |  |  |  | 0