## CEEGAAG SHALLOW WELL
BOQ FOR SUPPLY AND INSTALLATION OF SOLAR SYSTEM, SUBMERSIBLE PUMP, GENERATOR, GENERATOR ROOM, 20M3 ELEVATED WATER TANK, WELL REHABILITATION, ANIMAL TROUGHS, WATER KIOSK, FOR CEEGAG SHALLOW WELL HUDUN/SOOL REGION
SUPPLY AND INSTALLATION OF SOLAR SYSTEM AND SUBMERSIBLE PUMP
NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | Controller 2kw (Ameriacan or European) made. | unit | 1
2 | Submersible pump 0f (1.4kw - 8m3/hr - Maximum Head of 100m) Ameriacan or European) made. | unit | 1
3 | Solar panels 445W (Mono Crystalline). | pcs | 6
4 | Supply and construction of Module Support Structure for mounting the solar panels required to power the submersible pumps. The structure will be made of square hollow galvanized steel with vandal proofing anchored to the RC base in 800 mm deep hole 500 mm diameter), as shown in the drawing, including crane for pump lifting and lowering. | Lsm | 6
5 | Ac drop cable 10mm2 3-phase | m | 20
6 | PV cable 6mm single core | m | 20
7 | Well probe sensor for dry runing protection | unit | 1
8 | Surge Protector | unit | 1
10 | Cable splice kit 6-10mm2 | unit | 1
11 | Safety rope | m | 20
12 | PV Disconnect 440-40-6 | unit | 1
13 | High Presurre Pipes, Class B, 2" Diameter, 6m length c/w sockets | pcs | 10
16 | Fencing for Solar: 1. Supply and install mesh wire fence wall with 2inch angle bar spacing 2 meters c/c and hieght of 2.5 m(50cm shall go beneath earth ) The angle bars shall be fixed with a mass concrete footing having dimension of 0.3mx0.3mx0.5m 2. provide and fix Steel box gate of 1 meter wide and 2.5 m high fabricated from complete with all iron mongery and locking devices: including one coat of primer and two coats of approved paint. and Price to be included all nessecary tools and accessories for installing the fence wall. | LS | 1
TOTAL |  |  |  |  | 0
20M3 ELEVATED WATER TANK
NO | ITEM DESCRIPTION | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
1 | Excavation
Excavation including maintaining and supporting sides and keeping free from water, mud and fallen materials by bailing, pumping or otherwise
1.1 | Prepare site by stripping top 150 mm of soil to remove all debris including sand (if any) from site and carting away spoil. | m2 | 25
1.2 | Excavate trench commencing at reduced levels depth not exceeding 1.50m deep. | m3 | 18
1.3 | Pit excavation commencing at reduced levels depth not exceeding 1.50m deep | m3 | 7
1.4 | Remove surplus excavated material from site | m3 | 18
1.5 | Backfill around foundation | m3 | 6
Filing
1.6 | 300 mm thick approved hardcore filling spread, well rammed and compacted in 150mm layers | m3 | 7
Concrete work
Mass Concrete class 15 (1:3:6) with 20mm thick maximum aggregate size in
1.7 | 50mm Thick blinding. | m3 | 1.5
Vibrated Reinforced Concrete class 25 (1:1.5:3) with 20mm thick maximum aggregate size in
1.8 | Column Base / Footings (1500mm x 1500mm x 400mm) with Y16 reinforced bars spaced 20cm. | m3 | 4.5
1.9 | Ground Beam (400mm x 400mm) with Y16 reinforced bars spaced 20cm. | m3 | 2.5
Vibrated Reinforced Concrete class 25 (1:1.5:3) with 20mm thick maximum aggregate size in
1.1 | Two tie beams (400mm x 300mm) with Y16 reinforced bars spaced 20cm. | m3 | 5
1.11 | Columns (7.5m high from column base to the bottom of concrete slab (400mm x 400mm) with Y16 reinforced bars spaced 20cm. | m3 | 4.8
Vibrated Reinforced Concrete class 30 (1:1:2) with 20mm thick maximum aggregate size in
1.12 | 150mm thick Walls. | m3 | 5.25
1.13 | 200mm thick Base slab. | m3 | 2.4
1.14 | 150mm thick Cover slab. | m3 | 1.8
SUBTOTAL 1 |  |  |  |  | 0
2 | Finishes
Cement and sand mortar (1:3) rendering in:
2.1 | 25 mm Thick screed to base slab with waterproof cement | m2 | 12
2.2 | 15mm internal plaster to cover slab with waterproof cement | m2 | 12
2.3 | 15mm plaster to internal sides of wall with waterproof cement | m2 | 35
2.4 | 12mm plaster to external sides of wall | m2 | 35
2.5 | 12mm plaster to cover slab | m2 | 12
2.6 | 12mm plaster to soffits of base slab | m2 | 12
2.7 | 12mm plaster to beams | m2 | 45
2.8 | 12mm plaster to columns | m2 | 48
2.9 | Painting all plastered areas with two coats of preimier coat and two coats of offwite color. | m2 | 211
Water Supply System
Galvanized Mild Steel pipes class "B" medium thickness with and including jointing, fittings and fixe as described
| G.I Pipes: install 40 m outlet pipe, 40 inlet pipe, 3m overflow pipe, and 3m washout pipe | LS | 1
2.95 | 600x600x6mm heavy gauge steel primed metal manhole cover on slab with and including metal framing all around. | No | 2
2.96 | LADDER: Provide & fix steel ladder up to the top of the tank. | LS | 1
SUBTOTAL 2 |  |  |  |  | 0
COLLECTION
| SUBTOTAL 1 |  |  |  | 0
| SUBTOTAL 2 |  |  |  | 0
TOTAL COST OF 20M3 ELEVATED WATER TANK |  |  |  |  | 0
WELL REHABILITATION
NO | DESCRIPTION | UNIT | QUANTITY | RATE (USD) | AMOUNT (USD)
1 | Deepining of Shallow Well
1.1 | Excavate well shaft in soft and hard material to water rest level. | m | 3
1.2 | Dewatering of well to achieve optimal water depth. | m | 3
2 | Concrete works
2.1 | Supply and install 1500mm diameter reinforced Concrete rings/concret works in a vertical manner along the well shaft. | No. | 5
2.2 | Provide 150mm thick reinforced concrete slab using Y6 reinforcement spaced 30cm in both directions to mouth of well, apron and overflow drain. Cost to include, reinforcement, provision of inspection point with appropriate PC cover (600mmx600mm) to Engineer's specifications. | m³ | 1.35
3 | Wall Finishes
3.1 | 15mm cement and sand [1:3] render, finish with woodfloat to concrete or masonry surfaces. Screeds to be with water proof compound. | m² | 16
4 | Soak away pit
4.1 | Excavate pit to 1m wide and 1.5m depth. | m³ | 1.5
4.2 | Supply and Fill 2 Barrels of 200 litters. | m³ | 1.5
4.3 | Piping, construction of inlet chamber and RC suspended slab cover to pit. | m | 6
TOTAL OF WELL REHABILITATION |  |  |  |  | 0
400m EXTENSION PIPE TO ELEVATED WATER TANK
ITEM | ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
1 | EARTHWORKS
1.1 | Excavate trench in all materials include for joint holes, trimming sides and preparing trench bottom, backfill with part of the materials and compact. Depth of excavation 0.6m and width not less than 0.4m. | m³ | 72
1.2 | Backfilling either with insitu material or imported selected granular material for pipe surrounds and bedding as specified by the engineer. | m³ | 120
| SUBTOTAL 1 |  |  |  | 0
2 | PIPE WORK - PIPES
Supply, laying, test and commission the following:- PIPEWORK AND FITTINGS including All Joint Pipe Fittings all as required in the pipework installation. (elbows, nipples, sockets, gate valves, reducers, Tee PVC pipes, etc.)
2.1 | 2 inch UPVC Pipe (High Preasure Pipe) Class C | m | 400
| SUBTOTAL 2 |  |  |  | 0
TOTAL OF 500m EXTENSION PIPE TO ELEVATED WATER TANK |  |  |  |  | 0
CONSTRUCTION OF OPEN WATER KIOSK WITH 6 FAUCETS.
ITEM | ITEM DESCRIPTION | UNIT | Qty | RATE | AMOUNT
Excavation and Earthwork
1 | Excavate in soft material for foundation trenches not exceeding 250mm deep starting from stripped level | m3 | 2.4
| construction of water kiosk foundation using 200mm concrete hollow blocks with Cement mortar 1:6 (1 cement :6 coarse sand). | m2 | 5
Selected filling
2 | 250mm Thick hardcore filling compacted in layers not exceeding 150mm deep and well watered. | m3 | 2.4
3 | 50mm Thick quarry dust blinding to surfaces of hardcore (Measured Separately) | m2 | 0.5
Concrete work and Construction
Plain Concrete Class 15 / (1:3:6)
4 | 50 mm Thick slab on top of the laid hardcore. | m3 | 6
5 | 50mm thick concrete apron and drain channel | m3 | 1.7
6 | Construction of water kiosk wall using 200mm concrete hollow blocks with Cement mortar 1:6 (1 cement :6 coarse sand). | m2 | 5.5
Vibrated reinforced concrete class 25/20 with minimum cube crushing strength of 25N/mm² at 28 days
7 | 200mm 20/20 (1:2:4) RCC Capping. | m³ | 0.1
Mesh reinforcement ; B.S. 4483 ref A142 weighing 2.22 kgs per square meter including bends, tying wire and spacing blocks
8 | Fabric mesh reinforcement to ground floor slab | m2 | 12
Finishes
9 | Plaster (to wall, floor, etc) with cement and sand (1:6) mortar including rounding off or chamfering corners as directed and raking out joints including throating, nosing and drip course. | m² | 13
10 | Finishing wall with 100%Premium acrylic emulsion paint of approved brand and manufacture on wall surface, content including scraping and preparing the surface thoroughly, removing of dust etc all complete as permanufacturer's specification and direction of the site engineer. | m² | 13
Piping System
Supply, laying, test and commission the following:- PIPEWORK AND FITTINGS including All Joint Pipe Fittings all as required in the pipework installation. (elbows, nipples, sockets, gate valves, reducers, Tee PVC pipes, etc.)
11 | Excavate trench in all materials include for joint holes, trimming sides and preparing trench bottom, backfill with part of the materials and compact. Depth of excavation 0.5m and width not less than 0.4mm. | m³ | 3
12 | Backfilling either with insitu material or imported selected granular material for pipe surrounds and bedding as specified by the engineer. | m³ | 3
13 | 2 inch UPVC Pipe (High Preasure Pipe) Class C | m | 20
14 | Ditto but 1 inch | m | 12
15 | Taps 1" peglar | Nr | 6
16 | Gate valve 1" | Nr | 2
Soak away pit:
17 | Excavate (1000mm Diameter and 1500mm depth) soak pit, fill with granular material with high absorption capacity as shown in the drawing. | m3 | 1.2
Vibrated reinforced concrete class 25/20 with minimum cube crushing strength of 25N/mm² at 28 days
18 | 1100mm dia 75mm thick (1:2:4) soak pit cover slab. | No | 1
19 | Visibility board | Item | 1
TOTAL FOR CONSTRUCTION OF ONE WATER KIOSK |  |  |  |  | 0
ANIMAL TROUGH
B | ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
B1 | Site clearance and mobilization: should remove all waste and debris materials | LS | 1
B2 | Excavation trenches: excavate 500mm deep*1.25 wide *8.6 length for earth work. | CUM | 6
B3 | Foundation Blinding: Lay 50mm thick lean concrete 1:4:8 /3bags of cem/0.4cum of river sand /0.8cum of Graded stone 40mm nominal size AS PER SPECSabove the excavated footing and foundation trenchs, cure the blinding | CUM | 0.6
B4 | Hardcore: Supply and fill 300 mm selected hardcore stone and compact as per specification before recieving blinding | CUM | 3.5
B5 | Trough slab: Construction of RCC 150mm thick with meshwire sand, aggregate and cement ratio of 1:2:4 95% compacted over the foundation wall | CUM | 1.7
B6 | Construct masonry walls: construction of rubble stone masonry wall 0.25 m high x 0.2 thick in cement & sand mortar1:4 mix | CUM | 1
B7 | RCC BEAM:provide and cast 200mm X 100mm RCC with 1:2:4/6bags of cem/1cum of concrete___Reinforeced with Y12 linked with Y8mm stirupps @200mm c/c | CUM | 0.5
B8 | Wall Plaster: apply No 2 coats of 20mm thick plastering Mix 1:4 to intenal external walls including seiving sand and even finish as per line in levels , curing as per Field Engineer (2*19.7*0.35) | SQM | 14
B9 | white washing & Emulsion paint: apply No2 coats of emulsion paint to all int.and external of the trough (2*22*0.35) | SQM | 14
| FOOT STEP: laying o f 1.8 m slope slab Footstep around the goat trough for the animal to stand on it | CUM | 1.5
Total for One Animal Trough |  |  |  |  | 0
Total for Two Animal Trough |  |  |  | 2 | 0
ITEM | ITEM DESCRIPTION | UNIT | QUANTITY | RATE [USD] | AMOUNT [USD]
1 | POWER HYBRID SYSTEM (SOLAR & GENERATOR | No | 1 | 0 | 0
2 | 20M3 RCC ELEVATED WATER TANK | No | 1 | 0 | 0
4 | WELL REHABILITATION | No | 1 | 0 | 0
5 | PIPE EXTENSION | No | 1 | 0 | 0
6 | Water Kiosk | No | 1 | 0 | 0
7 | Animal Trough | No | 2 | 0 | 0
GRAND TOTAL FOR CEEGAG SHALLOW WELL HUDUN/SOOL |  |  |  |  | 0